READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Mechanical Insulation” Work is shown in the Contract Documents. Work to include ductwork insulation, duct liner insulation jackets, equipment insulation, covering, breeching insulation, thermal insulation for piping systems including vapor retarders, jackets and accessories, and liquid storage vessels and accessories.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - ASTM (American Society for Testing and Materials)

        - ASTM A167 - Standard Specification for Stainless and Heat-Resisting Chromium-Nickel Steel Plate, Sheet, and Strip.

        - ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate (ASTM B209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate).

        - ASTM C177 - Standard Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded Hot Plate Apparatus.

        - ASTM C195 - Standard Specification for Mineral Fiber Thermal Insulating Cement.

        - ASTM C449/C449M - Standard Specification for Mineral Fiber Hydraulic-Setting Thermal Insulating and Finishing Cement.

        - ASTM C518 - Standard Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus.

        - ASTM C533 - Standard Specification for Calcium Silicate Block and Pipe Thermal Insulation.

        - ASTM C534 - Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form.

        - ASTM C547 - Standard Specification for Mineral Fiber Preformed Pipe Insulation.

        - ASTM C552 - Standard Specification for Cellular Glass Thermal Insulation.

        - ASTM C553 - Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications.

        - ASTM C591 - Standard Specification for Unfaced Preformed Rigid Cellular Polyurethane Thermal Insulation.

        - ASTM C592 - Standard Specification for Mineral Fiber Blanket Insulation and Blanket-Type Pipe Insulation (Metal-Mesh Covered) (Industrial Type).

        - ASTM C610 - Standard Specification for Expanded Perlite Block and Pipe Thermal Insulation.

        - ASTM C612 - Standard Specification for Mineral Fiber Block and Board Thermal Insulation.

        - ASTM C795 - Standard Specification for Thermal Insulation for Use in Contact with Austenitic Stainless Steel.

        - ASTM C1071 - Standard Specification for Fibrous Glass Duct Lining Insulation (Thermal and Sound Absorbing Material).

        - ASTM C1126- Standard Specification for Faced or Unfaced Rigid Cellular Phenolic Thermal Insulation.

        - ASTM C1136 - Standard Specification for Flexible, Low Permeance Vapor Retarders for Thermal Insulation.

        - ASTM D1784 - Standard Specification for Rigid Poly (Vinyl Chloride) (PVC) Compounds and Chlorinated Poly (Vinyl Chloride) (CPVC) Compounds.

        - ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials.

        - ASTM E96 - Standard Test Methods for Water Vapor Transmission of Materials.

        - ASTM E162 - Standard Test Method for Surface Flammability of Materials Using a Radiant Heat Energy Source.

        - ASTM G21 - Standard Practice for Determining Resistance of Synthetic Polymeric Materials to Fungi.

      - FM (Factory Mutual Standards)

        - Factory Mutual Standards

      - Federal Specification (Insulation, Blankets, Thermal (Mineral Fiber, Industrial Type)

        - HH-I-558

      - Military Specification

        - MIL-I-22344

      - NFPA (National Fire Protection Association)

        - NFPA Standard 255

      - NAIMA (North American Insulation Manufacturers Association)

        - NAIMA - National Insulation Standards.

      - SMACNA (Sheet Metal and Air Conditioning Contractors’ National Association)

        - SMACNA - HVAC Duct Construction Standards - Metal and Flexible.

      - UL (Underwriters Laboratories, Inc.)

        - Underwriters Laboratories Standards

        - UL Standard 723 – Standard for Test for Surface Burning Characteristics of Building Materials

      - IFC (International Fire Code)

        - International Fire Code

      - IMC (International Mechanical Code)

        - International Mechanical Code

      - UPC (Uniform Plumbing Code)

        - Uniform Plumbing Code

      - Washington State Energy Code

        - Washington State Energy Code

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: Provide product description, thermal characteristics and list of materials and thickness for each service, and locations.

      - Manufacturer's Installation Instructions: Indicate installation procedures that ensure acceptable workmanship and installation standards will be achieved.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience.

    - Applicator: Company specializing in performing Work of this section with minimum three years experience.

    - At least one quality assurance person shall be present at all times during execution of all portions of the Work. This person shall be thoroughly familiar with the type of materials being installed and the best methods for their installation.

  - DELIVERY, STORAGE, AND HANDLING

Identify any special delivery, storage or handling requirements.

    - Accept materials on site in original factory packaging, labeled with manufacturer's identification, including product density and thickness

    - Protect insulation from weather and construction traffic, dirt, water, chemical, and mechanical damage, by storing in original wrapping.

  - ENVIRONMENTAL REQUIREMENTS

    - Do not install insulation outside ambient conditions required by manufacturer of each product.

    - Maintain temperature during and after installation for minimum period of 24 hours.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - GENERAL

    - Manufacturers: Armstrong, Johns-Manville, Owens-Corning, Knauf GmbH, Pittsburgh Corning, Armacell, Or Approved Equal.

    - Insofar as practicable, the products hereinafter described shall be of one manufacturer and shall meet the following requirements listed as to their function.

    - Insulation thickness is based on insulation having a thermal resistance of 4.0 to 4.6 per inch of thickness at a mean temperature of 75 degree F. Insulation thickness shall be increased or decreased for materials having R values less than 4.0 per inch or greater than 4.6 per inch.

    - High Temperature Piping: On piping systems where operating temperatures exceed 400F, provide calcium silicate with 6 oz. canvas jacket, l l/2 inch thick through 4 inch pipe, 2 inch thick over 4 inch pipe. Use insulation manufacturer's approved tape or joining methods.

    - Tape: Pressure sensitive lap of facing material. No duct tape will be used for joining or holding insulation service. Use insulation manufacturer's approved tape or joining methods.

    - Adhesive: Foster, Sealfos #30-36, Arabol, Armstrong 520, Or Approved Equal.

  - MAN MADE MINERAL FIBER

    - Insulation: ASTM C547 Mineral Fiber Pipe Insulation, [Type I 850(454) ___], [Type II 1200(650) ___], [Type III 1200(650) ___]. Manville Micro-Lok. Conform to ASTM C795 for application on Austenitic stainless steel [___].

The following insulation is suitable for nominal pipe sizes of 10 inches and larger.

    - Insulation: ASTM C795; semi-rigid, noncombustible, end grain adhered to jacket.

      - ‘K’ factor: ASTM C177, [0.24 at 75 degrees F] [___ at 75 degrees F].

      - Maximum service temperature: [650 degrees F] [___ degrees F].

      - Maximum moisture absorption: 0.2 percent by volume.

    - Vapor Retarder Jacket:

      - [ASTM C921] White kraft paper with glass fiber yarn, bonded to aluminized film.

      - Moisture vapor transmission: ASTM E96; 0.02 perm-inches.

    - Tie Wire: 0.048 inch stainless steel with twisted ends on maximum 12 inch centers.

Include the following paragraph for vapor retarder lap adhesive used to seal laps and joints of vapor retarder jacket.

    - Vapor Retarder Lap Adhesive:

      - Compatible with insulation.

    - Insulating Cement/Mastic:

      - ASTM C195; hydraulic setting on mineral wool.

    - Fibrous Glass Fabric:

      - Cloth: Untreated; 9 oz/sq yd weight.

      - Blanket: 1.0 lb/cu ft density.

      - Weave: [5x5] [10x10] [10x20].

Include the following paragraph for indoor vapor retarder finish used to finish over insulation.

    - Indoor Vapor Retarder Finish:

      - Cloth: Untreated; 9-oz/sq yd weight.

      - Vinyl emulsion type acrylic, compatible with insulation, [black] [white] [___] color.

Include the following paragraph for outdoor vapor retarder mastic used as a coating over insulation with a reinforcing fabric.

    - Outdoor Vapor Retarder Mastic:

      - Vinyl emulsion type acrylic or mastic, compatible with insulation, black color.

    - Outdoor Breather Mastic:

      - Vinyl emulsion type, black acrylic or mastic, compatible with insulation.

    - Insulating Cement:

      - ASTM C449/C449M.

  - MAN MADE MINERAL FIBER, FLEXIBLE BLANKET OR BATTS

    - Insulation: ASTM C553; Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications. [Type I] [___], or [Type II] [___], or [Type III [___].

    - Vapor Retarder Jacket: ASTM 1136, Type II Flexible and Low Permeance Vapor Retarders for Thermal Insulation.

      - For systems operating at temperatures below ambient, close and secure seams and joints. If outward clinching staples are used, then the staple penetrations must also be sealed.

    - Tie Wire: 0.048 inch stainless steel with twisted ends on maximum 12 inch centers.

Include the following paragraph for vapor barrier lap adhesive used to seal laps and joints of vapor barrier jacket.

    - Vapor Retarder Lap Adhesive:

      - Compatible with insulation.

    - Insulating Cement/Mastic:

      - ASTM C195; hydraulic setting on mineral wool.

    - Exposed Supply and Outside Air Ductwork:

      - Method: 2 inch rigid board with minimum thermal resistance of R-7 on metal fasteners at l2 inch O.C. weather proof and vapor proof laminated jacket continuously sealed longitudinal joints and taped connection joints, (6 oz. canvas finished jacket in mechanical rooms and/or portion of duct in occupied areas which is within 9 foot-0 inches of finished floor).

    - Concealed Supply and Outside Air Ductwork:

      - Method: 2", 3.0 lb blanket with foil.

  - MINERAL FIBER, FLEXIBLE INSULATION FOR THE EXTERIOR OF SHEET METAL DUCTS

    - Insulation: ASTM C553 Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications, Type II.

    - Vapor Retarder Jacket:

      - [Kraft paper with glass fiber yarn and bonded to aluminized film] [0.0032 inch vinyl].

      - Moisture vapor transmission: ASTM E96; [0.02] [1.3] perm.

      - Secure with pressure sensitive tape.

    - Vapor Retarder Tape:

      - Kraft paper reinforced with glass fiber yarn and bonded to aluminized film, with pressure sensitive rubber based adhesive.

Include the following paragraph for outdoor vapor barrier mastic used as a coating over insulation with a reinforcing fabric.

    - Outdoor Vapor Retarder Mastic:

      - Vinyl emulsion type acrylic or mastic, compatible with insulation, black color.

    - Tie Wire: Annealed steel, 16 gage.

  - MINERAL FIBER, RIGID INSULATION FOR THE EXTERIOR OF SHEET METAL DUCTS

    - Insulation: ASTM C612 Mineral Fiber Block and Board Insulation, Type IA

    - Vapor Retarder Jacket:

      - [Kraft paper with glass fiber yarn and bonded to aluminized film] [0.0032 inch vinyl].

      - Moisture vapor transmission: ASTM E96; [0.04] [1.3] perm.

      - Secure with [pressure sensitive tape] [two coats of vapor barrier mastic and glass tape].

    - Vapor Retarder Tape:

      - Kraft paper reinforced with glass fiber yarn and bonded to aluminized film, with pressure sensitive rubber based adhesive.

    - Indoor Vapor Retarder Finish:

      - Cloth: Untreated; 9 oz/sq yd weight, glass fabric.

      - Vinyl emulsion type acrylic, compatible with insulation, [black] [white] [___] color.

    - Exposed Supply and Outside Air Ductwork:

      - Method: 2 inch rigid board with minimum thermal resistance of R-7 on metal fasteners at l2 inch O.C. weather proof and vapor proof laminated jacket continuously sealed longitudinal joints and taped connection joints, (6 oz. canvas finished jacket in mechanical rooms and/or portion of duct in occupied areas which is within 9 foot 0 inches of finished floor).

  - CELLULAR GLASS

    - Insulation: ASTM C552, Type II - pipe and tubing insulation, Class 2 - Jacketed.

      - ‘K’ factor: ASTM C177 or ASTM C518, [0.29] [___] at 75 degrees F.

    - Preformed Glass Fiber Pipe Insulation:

      - 4 lb. density

      - HH-I-558, Form D, Type III, Class l2 (to 450F), Class l3 (to 500F)

      - MIL-I-22344

      - ASTM C 547

    - Blanket Type Flexible Glass Fiber: Blanket type flexible glass fiber insulation shall be R6. (Duct Installation) ASTM C553, Type 1, Classes B-2 through B-5.

    - Blanket Type, Flexible Glass Fiber, R6,

    - HH-I-558, Form B, Type I (Duct Insulation)

    - ASTM 553, Type l, Class B-2 through B-5

    - Concealed Supply, Return and Outside Air Ductwork: Such ductwork shall have flexible glass-fiber blanket insulation for outside of duct, two inches thick, of 1.5-pound density, with foil-scrim-kraft facing, R-8 thermal resistance; conforming to the requirements of MIL-I-22023 or ASTM C553.

  - GLASS FIBER, RIGID

    - Insulation: ASTM C612 or ASTM C592; rigid, noncombustible.

      - ‘K’ factor: ASTM C177 or ASTM C518, [0.24] [___] at 75 degrees F.

      - Maximum Service Temperature: [450] [650] [850] [___] degrees F.

      - Maximum Moisture Absorption: 0.1 percent by volume.

      - Density: [1.0] [2.0] [3.0] [___] lb/cuft.

    - Rigid Board Glass Fiber

      - 6 lb density

      - HH-I-558, Form A, Class 2

    - Vapor Retarder Jacket: ASTM C1136 Flexible, Low Permeance Vapor Retarders for Thermal Insulation, Type II.

    - Facing: 1 inch [galvanized] [stainless] steel hexagonal wire mesh stitched [on one face of insulation] [onto both faces of insulation] [on one face of insulation with expanded metal lath on other].

Include the following paragraph for vapor barrier lap adhesive used to seal laps and joints of vapor barrier jacket.

    - Vapor Retarder Lap Adhesive:

      - Compatible with insulation.

    - Insulating Cement/Mastic:

      - ASTM C195; hydraulic setting on mineral wool.

Choose between two alternatives for Domestic Cold Water, Rainleaders and Roof Drain Bowls. One choice is in paragraph 2.6F below; the other is under 2.14B.

    - Domestic Cold Water, Rainleaders and Roof Drain Bowls:

      - Insulation for such equipment shall be preformed glass fiber, 1/2 inch thick, of four pound density, with factory-applied jacket and pressure-sensitive tape closure system.

      - Conforming to the requirements of MIL-I-22344 or ASTM C547.

      - Manville Micro-Lok, Owens-Corning Fiberglas II, Or Approved Equal.

    - Chilled Water Piping:

      - Insulation for chilled water piping shall be preformed glass fiber, one inch thick, four pound density, with factory-applied jacket and pressure-sensitive tape closure system.

      - Conforming to the requirements of MIL-I-22344 or ASTM C547.

      - For all lines use 1-1/2 inch thick insulation with vapor seal.

    - Fire Protection Water: Apply one inch thick preformed glass fiber as specified under paragraph G above over electric heat tape in unheated spaces where indicated on the drawings

Choose between two alternatives for Domestic Hot Water, Circulating Hot Water, or Hot Water Piping. One choice is in paragraph 2.6I below; the other is under 2.14C.

    - Domestic Hot Water, Circulating Hot Water, or Heating Water Piping: Insulation for these piping types shall be preformed glass fiber, four pound density, with factory-applied jacket and pressure-sensitive tape closure system; conforming to the requirements of MIL-I-22344 or ASTM C547.  For 1/2 inch to 1 inch pipe use 1 1/2 inch thick, 1 1/4 inch to 2 inch pipe use 2 inch thick, and for 2 1/2 inch to 4 inch pipe use 2 1/2 inch thick.

    - Low Pressure Steam (to 500 degrees F) and Condensate: Insulation for low pressure steam and condensate piping shall be preformed glass fiber, [   ] inch thick, of four pound density, with factory-applied jacket and pressure-sensitive tape closure system; conforming to the requirements of MIL-I-22344 or ASTM C547. Manville Micro-Lok, Owens-Corning Fiberglas II, Or Approved Equal.

  - EXPANDED PERLITE

    - Molded Expanded Perlite Block and Pipe Insulation: ASTM C610, Pipe Insulation.

  - HYDROUS CALCIUM SILICATE

    - Calcium Silicate Block and Pipe Thermal Insulation: ASTM C533, Type II - for use on surfaces up to 1200 degrees F.

    - Rigid block and asbestos free:

      - HH-I-523, Type l

      - ASTM C 533

    - Tie Wire: 0.048 inch stainless steel with twisted ends on maximum 12 inch centers.

    - Mineral Fiber Hydraulic-Setting Thermal Insulating and Finishing Cement:

      - ASTM C449/C449M.

    - High Pressure Steam (over 500 degrees F): Insulation for high pressure steam piping shall be molded, sectioned, hydrous calcium silicate; [___] inch thick for pipe up to [___] inch; [___] inch thick for pipe over [___] inch; with factory-applied canvas jacket; conforming to the requirements of MIL-I-2781, Grade I, II or III, or ASTM C533.

  - CELLULAR POLYISOCYANURATE THERMAL INSULATION

    - Unfaced Preformed Rigid Cellular Polyisocyanurate Thermal Insulation: ASTM C591, Type III, compressive strength 50 psi

Polyurethane is defined as the same as polyisocyanruate.

    - Rigid Polyurethane Pipe Insulation

      - Continuously molded rigid polyurethane

        - 0.l6K at 75F,

        - HH-I-l75l/4, Type II, Grade II

        - ASTM C 518

  - CELLULAR PHENOLIC FOAM

    - Faced or Unfaced Rigid Cellular Phenolic Pipe and Board Thermal Insulation, ASTM C1126, Type II and Type III.

  - ELASTOMERIC CELLULAR FOAM

    - Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular form: ASTM C534;

      - Type I, Tubular form

    - Foamed Plastic, 0.27K at 75F:

      - HH-I-573

      - MIL-P-l5280

      - ASTM C 534

Choose between two alternatives for Domestic Cold Water, Rainleaders and Roof Drain Bowls. One choice is in paragraph 2.6F above; the other is in 2.14B below.

    - Domestic Cold Water, Rainleaders and Roof Drain Bowls: Insulation for such equipment shall be foamed plastic, 3/8 inch thick, 0.27K at 75 degrees F; conforming to the requirements of MIL-P-15280 or ASTM C534.

Choose between two alternatives for Domestic Hot Water, Circulating Hot Water, or Hot Water Piping. One choice is in paragraph 2.6I above; the other is under 2.14C below.

    - Domestic Hot Water, Circulating Hot Water, or Heating Water Piping: Insulation for these piping types shall be foamed plastic, 1/2 inch thick, 0.27K at 75 degrees F; conforming to the requirements of MIL-P-15280 or ASTM C534.

Include the following paragraph for elastomeric foam adhesive used to bond seams and joints in elastomeric foam insulation.

    - Elastomeric Foam Adhesive:

      - Air dried, contact adhesive, compatible with insulation.

  - JACKETS

    - PVC Pipe Jacket: [ASTM D1784,] one piece molded type fitting covers and sheet material, off-white color.

      - Thickness: [10] [15] [30] mil.

      - Connections: [Brush on welding adhesive] [Tacks] [Pressure sensitive color matching vinyl tape].

    - PVC Equipment Jacket: Sheet material, off-white color.

      - Minimum Service Temperature: [-40] [___] degrees F.

      - Maximum Service Temperature: [150] [___] degrees F.

      - Moisture Vapor Transmission: ASTM E96; 0.002 perm-inches.

      - Thickness: [10] [15] [20] [30] mil.

      - Connections: [Brush on welding adhesive] [Tacks] [Pressure sensitive color matching vinyl tape].

Include the following paragraph for PVC covering adhesive mastic used to seal laps and joints of PVC covers.

    - Covering Adhesive Mastic:

      - Compatible with insulation.

The following jacket material meets USDA requirements for use in food processing plants but may not comply with ASTM E84 flame spread and smoke developed ratings.

    - ABS Plastic Jacket: One piece molded type fitting covers and sheet material, off-white color.

      - Minimum service temperature: [-40] [___] degrees F.

      - Maximum service temperature of [180] [___] degrees F.

      - Moisture vapor transmission: ASTM E96; 0.012 perm-inches.

      - Thickness: [30] [___] mil.

      - Connections: Brush on welding adhesive.

    - Canvas Jacket: UL listed.

      - Fabric: 6 oz/sq yd, plain weave cotton.

      - Fire retardant lagging adhesive. Composite of insulation, jacket and lagging adhesive shall have a flame spread index not greater than 25 and a smoke developed index not greater than 50 per ASTM E84.

Include the following paragraph for insulation lagging adhesive used to adhere canvas to insulation.

      - Lagging Adhesive:

        - Compatible with insulation.

    - Aluminum Jacket: ASTM B209.

      - Thickness: [0.016] [0.020] [0.025] [0.032] [0.040] [___] inch thick sheet.

      - Finish: [Smooth] [Embossed] [___].

      - Joining: Longitudinal slip joints and 2 inch laps.

      - Fittings: [0.016] [___] inch thick die shaped fitting covers with factory attached protective liner.

      - Metal Jacket Bands: 3/8 inch wide; [0.015] [___ inch thick aluminum] [0.010 ___ inch thick stainless steel].

    - Stainless Steel Jacket: ASTM A167 Type [302] [304] [316] stainless steel.

      - Thickness: [0.010] [0.016] [0.018] [___] inch thick.

      - Finish: [Smooth.] [Corrugated.]

      - Metal Jacket Bands: 3/8 inch wide; [0.010] [___] inch thick stainless steel.

    - Mineral Fiber (Outdoor Duct) Jacket: Asphalt impregnated and coated sheet, [50] [36] lb/square.

    - Jackets

      - Laminated: Kraft paper, aluminum foil NFPA 90A approved and 0.02 permeability, exterior layer kraft paper (All purpose.)

      - Canvas: 4 oz. factory applied, 6 oz. field applied.

      - Metal: (0.0l6 inch aluminum) or (0.0l0 inch stainless steel)

      - Asphaltic: Fibrated solvent asphalt waterproofsolvent asphalt waterproof.

  - GLASS FIBER DUCT LINER, FLEXIBLE INSULATION FOR THE INTERIOR OF SHEET METAL DUCTS

    - Insulation: ASTM C1071 Thermal and Acoustical Insulation (Glass Fiber, Duct Lining Material), Type I

    - Duct Liner, Flexible blanket type, 1/2 inch thick, 2.0 lb./cu. ft. density:

      - NFPA 90B

      - HH-I-545B, Type I

    - Fire Resistance:

      - Flame Spread (LT) 25, Fuel Contributed (LT) 50, Smoke Developed (LT) 50, per ASTM E-84, and UL 723.

    - Adhesive:

      - Waterproof [ASTM E162 fire-retardant] type.

      - Adhesive: Foster, Sealfos #30-36, Arabol, Armstrong 520, Or Approved Equal insulation adhesive.

    - Liner Fasteners: Galvanized steel, [self-adhesive pad] [impact applied] [welded] with [integral] [press-on] head.

    - Where duct liner is required, rigid fiberglass plenum liner board shall be used for inside of duct, one inch thick, of 1.5-pound density, with air stream surface covered with smooth, black, glass-fiber mat.

    - Pressure-sensitive duct tape of same material as insulation facing, three inches wide shall be used.

    - Calcium silicate, asbestos free, ASTM C449 or SS-C-l60, Type 3, Grade F insulating cement shall be used.

    - Exposed Supply, Return and Outside Air Ductwork:

      - Such ductwork shall have flexible glass-fiber blanket insulation for inside of duct, one inch thick, of 1.5-pound density, with air stream surface covered with smooth, black, glass-fiber mat.

  - GLASS FIBER DUCT LINER, BOARD INSULATION FOR THE INTERIOR OF SHEET METAL DUCTS

    - Insulation: ASTM C1071 Thermal and Acoustical Insulation (Glass Fiber, Duct Lining Material), Type II.

    - Duct Liner, Rigid type, 1 inch thick, 3.0 lb./cu. ft. density:

      - NFPA 90A and NFPA 90B

      - HH-I-545B Type II

    - Fire Resistance:

      - Flame Spread (LT) 25, Fuel Contributed (LT) 50, Smoke Developed (LT) 50, per ASTM E-84, and UL 723.

    - Adhesive:

      - Waterproof [ASTM E162 fire-retardant] type.

    - Liner Fasteners: Galvanized steel, [self-adhesive pad] [impact applied] [welded] with [integral] [press-on] head.

  - GLASS FIBER ROUND DUCT LINER

    - Insulation: Round, preformed in cylindrical sections with [polyvinyl acetate polymer] [acrylic polymer meeting ASTM G21] impregnated surface coat.

      - ‘K’ factor: ASTM C1071, [0.23] [___] at 75 degrees F.

      - Maximum service temperature: [250] [___] degrees F.

      - Maximum Velocity on Coated Air Side: [4,000] [5,000] [___] fpm.

- EXECUTION

  - EXAMINATION

    - Verify that piping, equipment and ductwork has been tested before applying insulation materials.

    - Verify that surfaces are clean and dry, with foreign material removed.

  - INSTALLATION

    - Install in accordance with NAIMA National Insulation Standards.

    - To prevent shrinkage, the covering shall be applied when the building is thoroughly dry.

    - Repair and/or replace damaged or removed covering on existing equipment and piping where damaged by Work under this contract.

    - All surfaces shall be insulated which would: reduce heat gain or loss, avoid undesirable condensation and/or reduce corrosion.

    - Exposed Piping: Locate insulation and cover seams in least visible locations. Finish exposed piping and equipment insulation with white pigmented lagging adhesive (not required on AP jacket finish). Equipment, piping, valves, etc., in boiler rooms, mechanical rooms and fan rooms are considered exposed whether in a plenum or not.

    - Pipe Exposed in Mechanical Equipment Rooms or Finished Spaces [(less than 10 feet above finished floor)]: Finish with [canvas jacket sized for finish painting] [PVC jacket and fitting covers] [ABS jacket and fitting covers] [aluminum jacket] [stainless steel jacket]. Piping within 8 foot 0 inches of Floor: Provide field applied 6 oz. canvas jacket. Finish with white pigmented lagging adhesive.

    - Insulated pipes conveying fluids below ambient temperature: Insulate entire system including fittings, valves, unions, flanges, strainers, flexible connections, [pump bodies,] and expansion joints. Apply insulating cement to all fittings, valves and strainers, equal to the adjacent thickness. Cover with four ounce canvas jackets or preformed PVC fitting covers.

    - Man made mineral fiber insulated pipes conveying fluids below ambient temperature:

      - Provide factory-applied or field-applied vapor retarder jackets. Secure factory-applied jackets with pressure sensitive adhesive self-sealing longitudinal laps and butt strips. Secure field-applied jackets with outward clinch expanding staples and seal all staple penetrations with vapor retarder mastic.

      - Insulate fittings, joints, and valves with molded insulation of like material and thickness as adjacent pipe. Finish with glass cloth and vapor retarder adhesive or PVC fitting covers.

    - For hot piping conveying fluids over [140] [___] degrees F, insulate flanges and unions at equipment.

    - Man made mineral fiber insulated pipes conveying fluids above ambient temperature:

      - Provide factory-applied or field-applied standard jackets. Secure with outward clinch expanding staples or the pressure sensitive adhesive system on standard factory-applied jacket and butt strips or both.

      - Insulate fittings, joints, and valves with insulation of like material and thickness as adjoining pipe. Finish with glass cloth and adhesive or PVC fitting covers.

    - Inserts and Shields:

      - Application: Piping or Equipment [1 1/2] [2] [___] inches diameter or larger.

      - Shields: [Galvanized] steel between pipe hangers or pipe hanger rolls and inserts.

      - Insert location: Between support shield and piping and under the finish jacket.

      - Insert configuration: Minimum 6 inches long, of same thickness and contour as adjoining insulation; may be factory fabricated.

      - Insert material: Compression resistant insulating material suitable for the planned temperature range and service.

      - Protective Saddle: Insulate under pipe hangers (full thickness) and provide l8 gage galvanized protective saddles covering lower half of insulation. Protective saddle length equal to pipe size with 6 inches minimum length. Use high density insulation insert on pipe 2 inch and larger.

    - Continue insulation through penetrations of building assemblies or portions of assemblies having a fire resistance rating of one hour or less. Provide intumescent firestopping when continuing insulation through assembly. Finish at supports, protrusions, and interruptions. See Section 07 84 00 - Firestopping for penetrations of assemblies with a fire resistance rating greater than one hour.

    - Exterior Applications: Provide vapor retarder jacket. Insulate fittings, joints, and valves with insulation of like material and thickness as adjoining pipe, and finish with glass mesh reinforced vapor retarder cement. Cover with [aluminum] or [stainless steel] jacket with waterproof joints and seams and with seams located at the 3 or 9 o’clock position on the side of horizontal piping with the overlap facing down to shed water or on the bottom side of horizontal equipment.

    - Buried Piping: Insulate only where the manufacturer of a specific insulation recommends that their product may be installed either in a trench, tunnel or direct buried. Provide factory fabricated assembly with inner all-purpose service jacket with self-sealing lap, and asphalt impregnated open mesh glass fabric, with 1 mil thick aluminum foil sandwiched between three layers of bituminous compound; outer surface faced with a polyester film.

    - Double insulation thickness for all lines buried, in outside tunnels or where exposed to outside temperatures.

    - Insulation not required for rain leaders, underground, in tunnels, in crawl spaces, or in unexcavated areas.

    - Do not insulate direct burial cold water.

    - Heat Traced Piping:

      - Insulate fittings, joints, and valves with insulation of like material, thickness, and finish as adjoining pipe. Provide a size large enough to enclose pipe and heat tracer. Cover with [aluminum] [stainless steel] jacket with seams located at the 3 or 9 o’clock position on the side of horizontal piping with the overlap facing down to shed water.

    - Factory Insulated Equipment: Do not insulate.

    - Exposed Equipment: Locate insulation and cover seams in least visible locations. Exposed piping and equipment shall be finished with white-pigmented lagging adhesive (not required on AP jacket finish).

    - Insulation is not required on sound-lined ductwork.

    - Apply insulation close to equipment by grooving, scoring, and beveling insulation. Fasten insulation to equipment with studs, pins, clips, adhesive, wires, or bands.

    - Fill joints, cracks, seams, and depressions with bedding compound to form smooth surface. On cold equipment, use vapor retarder cement.

    - Insulated equipment that contains fluids below ambient temperature: Insulate entire system.

    - Mineral fiber insulated equipment that contains fluids below ambient temperature: Provide vapor retarder jackets, factory-applied or field-applied. Finish with glass-cloth and vapor barrier adhesive.

    - For hot equipment that contains fluids over [140] [___] degrees F, insulate flanges and unions with removable sections and jackets.

    - Mineral fiber insulated equipment that contains fluids above ambient temperature: Provide standard jackets, with or without vapor retarder, factory-applied or field-applied. Finish with glass cloth and adhesive.

    - Finish insulation at supports, protrusions, and interruptions.

    - Equipment in Mechanical Equipment Rooms or Finished Spaces: Finish with [canvas jacket sized for finish painting] [PVC jacket and fitting covers] [aluminum jacket] [stainless steel jacket].

    - Nameplates and ASME Stamps: Bevel and seal insulation around; do not insulate over.

    - Equipment Requiring Access for Maintenance, Repair, or Cleaning: Install insulation so it can be easily removed and replaced without damage.

    - Insulated ductwork conveying air below ambient temperature:

      - Provide insulation with vapor retarder jackets.

      - Finish with tape and vapor retarder jacket.

      - Continue insulation through walls, sleeves, hangers, and other duct penetrations.

      - Insulate entire system including fittings, joints, flanges, fire dampers, risers, branches, flexible connections, and expansion joints.

    - Insulated ductwork conveying air above ambient temperature:

      - Provide with or without standard vapor retarder jacket.

      - Insulate fittings and joints. Where service access is required, bevel and seal ends of insulation.

    - Ductwork Exposed in Mechanical Equipment Rooms or Finished Spaces [(below 10 feet above finished floor)]: Finish with [canvas jacket sized for finish painting] [aluminum jacket].

    - Exterior Applications: Provide insulation with vapor retarder jacket. Cover with [outdoor jacket finished as specified in Section ___] [with caulked aluminum jacket with seams located on bottom side of horizontal duct section].

    - External Duct Insulation Application:

      - Secure insulation with vapor retarder with wires and seal jacket joints with vapor retarder adhesive or tape to match jacket.

      - Secure insulation without vapor retarder with staples, tape, or wires.

      - Install without sag on underside of ductwork. Use adhesive or mechanical fasteners where necessary to prevent sagging. Lift ductwork off trapeze hangers and insert spacers.

      - Seal vapor retarder penetrations by mechanical fasteners with vapor retarder adhesive.

      - Stop and point insulation around access doors and damper operators to allow operation without disturbing wrapping.

      - Insulate supply and return ductwork exposed to the weather as noted for exposed supply ductwork and finish cover with (2) two 1/8 inch coats of mastic, reinforced with glass fabric. (Lap all seams and joints 2 inches).

Duct liner is specified in this section. If the installation is relocated to ductwork sections, delete the references from here and relocate.

    - Duct [and Plenum] Liner Application:

      - Adhere insulation with adhesive for [90] [100] percent coverage.

      - Secure insulation with mechanical liner fasteners. SMACNA Standards for spacing.

      - Seal and smooth joints. Seal and coat transverse joints.

      - Seal liner surface penetrations with adhesive.

      - Duct dimensions indicated are net inside dimensions required for airflow. Increase duct size to allow for insulation thickness.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Sole Source