READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

  - The extent and location of “Dry-Pipe Fire Suppression Sprinkler” Work is shown in the Contract Documents.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - NFPA 13 (National Fire Protection Association) Installation of Sprinkler Systems

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Shop Drawings: Indicate layout of finished ceiling areas indicating sprinkler locations coordinated with ceiling installation. Indicate detailed pipe layout, hangers and supports, sprinklers, components and accessories. Indicate system controls.

      - Product Data: Submit data on sprinklers, valves, pumps, compressors and specialties, including manufacturers catalog information. Submit performance ratings, rough-in details, weights, support requirements, and piping connections.

Include the following paragraph for submission of physical samples for selection of finish, color, texture, etc. Edit number and sizes of samples if necessary.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

  - SYSTEM DESCRIPTION

Use this article carefully; restrict statements to describe components used to assemble the system. Do not repeat statements made in the SUMMARY article; “Section includes” paragraph.

    - System to provide coverage for [entire building] [building areas noted] [building areas noted in Schedule] [___].

    - Provide [hydraulically designed] system to [NFPA 13] [light hazard] [ordinary hazard, Group 1] [ordinary hazard, Group 2] [ordinary hazard, Group 3] [extra hazard] occupancy requirements.

    - Schedule 40 is the minimum, NO EXCEPTIONS, acceptable wall thickness by the Port of Seattle for fire suppression sprinklers piping.

    - Provide hot dipped galvanized piping for dry-pipe suppression sprinklers.

    - Determine volume and pressure of incoming water supply from water flow test data. If not available assume [___] gpm at [___] psig. Revise design when test data become available prior to submittals.

    - Interface system with [building control system] [building fire and smoke alarm system] [___].

    - Provide fire department connections [where indicated] [___].

  - QUALITY ASSURANCE

    - Perform Work in accordance with [NFPA 13] [State of Washington] [City of SeaTac] [City of Seattle] regulations.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years [documented] experience.

    - Installer: Company specializing in performing Work of this section with minimum three years [documented] experience [approved by manufacturer]. [SeaPort only add the following: Installation fitter must have valid SFD AS-1 license.]

    - Design system under direct supervision of a Professional Engineer experienced in design of this Work and licensed in the State of Washington.

  - DELIVERY, STORAGE, AND HANDLING

Identify any special delivery, storage or handling requirements.

    - Store products in shipping containers until installation. Provide and maintain temporary inlet and outlet caps until installation.

  - WARRANTY

This article extends the manufacturer’s warranty period beyond one year. Extended warranties add to the construction costs and may present difficulties to the Owner in enforcing them. Specify with caution.

    - Provide [five] [___] year manufacturer warranty for air compressor and pump.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Supply extra sprinklers under provisions of [NFPA 13].

Supply suitable wrenches for each sprinkler type.

Supply metal storage cabinet [in location designated] [adjacent to alarm valve] [___].

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - SPRINKLERS

    - Perform Work in accordance with [NFPA 13] [State of Washington] [City of SeaTac] [Port of Seattle] regulations.

Edit the following descriptive specifications to identify Project requirements and to eliminate any conflict with manufacturers (products) specified above.

    - Suspended Ceiling Type:

      - Type: [Standard] [Semi-recessed] [Recessed] [Concealed] pendant type with matching [push on] [clamp on] [screw on] escutcheon plate. Reliable F1FR (wet)/F3QR (dry), Viking Microfast series/QREC, Or Approved Equal.

      - Finish: [Brass.] [Chrome plated.] [Enamel, color ___] [as selected].

      - Escutcheon Plate Finish: [Brass.] [Chrome plated.] [Enamel, color ___] [as selected].

      - Fusible Link: [Fusible-solder link type] [Glass bulb type] temperature rated for specific area hazard.

    - Exposed Area Type:

      - Type: Standard upright type [with guard].

      - Finish: [Brass.] [Chrome plated.] [Enamel, color ___] [as selected].

      - Fusible Link: [Fusible-solder link type] [Glass bulb type] temperature rated for specific area hazard.

    - Side wall Type:

      - Type: [Standard] [Semi-recessed] [Recessed] horizontal side wall type with matching [push on] [clamp on] [screw on] [escutcheon plate and guard]. Reliable F3QR (Dry), Viking Microfast series/QREC, Or Approved Equal.

      - Finish: [Brass] [Chrome plated] [Enamel, color ___] [as selected].

      - Escutcheon Plate Finish: [Brass.] [Chrome plated.] [Enamel, color ___] [Nickel plated.] [as selected] and painted by manufacturer.

      - Fusible Link: [Fusible-solder link type] [Glass bulb type] temperature rated for specific area hazard.

    - Guards: Finish to match sprinkler finish.

  - AIR COMPRESSOR

    - Perform Work in accordance with [NFPA 13] [State of Washington] [City of SeaTac] [City of Seattle] regulations.

Edit the following descriptive specifications to identify Project requirements and to eliminate any conflict with manufacturers (products) specified above.

    - Compressor: Single unit, electric motor driven, motor, motor starter, safety valves, check valves, air maintenance device incorporating electric pressure switch and unloading valve.

    - Must fill system to capacity within 30 minutes (Per NFPA 13 section 7.2.6.2.2)

- EXECUTION

  - INSTALLATION

    - Perform Work in accordance with [NFPA 13] [State of Washington] [City of SeaTac] [Port of Seattle] [City of Seattle] regulations.

    - Locate fire department connection with sufficient clearance from walls, obstructions, or adjacent Siamese connectors to allow full swing of fire department wrench handle. If possible SFD would like to see the FDC located 40’ from the structure

    - Locate outside alarm-gong on building wall [as indicated.] [___]

    - Place pipe runs to minimize obstruction to other Work.

    - Place piping in concealed spaces above finished ceilings.

Coordinate sprinkler layout with the reflected ceiling plan and edit the following paragraph as appropriate. Note that center of tile location increases cost as a pipe offset is required at each end.

    - Center sprinklers in [two directions in ceiling tile and provide piping offsets as required] [one direction only in ceiling tile with location in other direction variable, dependent upon spacing and coordination with ceiling elements] [___].

    - Perform Work in accordance with [NFPA 13] [State of Washington] [City of SeaTac] [Port of Seattle] regulations.

    - Install guards on sprinklers located below 7” or [where indicated] [___].

    - Install air compressor on vibration isolators. Refer to Section 20 05 48 - Mechanical Sound, Vibration, and Seismic Control.

    - Hydrostatically test entire system.

    - Require test be witnessed by [Fire Marshall.] [Authority having jurisdiction.] [Owner's insurance underwriter.] [Architect/Engineer.] [___].

  - INTERFACE WITH OTHER PRODUCTS

    - Ensure required devices are installed and connected as required to fire alarm system.

  - CLEANING

    - Section 01 74 00 - Cleaning.

    - Flush entire piping system of foreign matter.

  - PROTECTION OF INSTALLED CONSTRUCTION

    - Protect sprinklers to ensure concealed sprinklers, cover plates, and sprinkler escutcheons do not receive field paint finish. Remove after painting.

    - Contractor responsible to replace sprinklers that get overspray, paint, or other foreign material that renders them out of compliance with NFPA requirements.

    - Any new sprinklers installed under this contract required to be replaced due to damage by the project Work shall be replaced at no cost to the owner.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2