READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Unitary Air Conditioning Equipment” Work is shown in the Contract Documents. Section includes packaged roof top unit, unit controls, remote panel, roof mounting curb and base, maintenance service, unitary air conditioners and controls. Packaged terminal air conditioning units, wall sleeves and louvers and controls.

  - GOVERNING CODES, STANDARDS AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - ARI (Air Conditioning and Refrigeration Institute)

        - ARI 210 - Unitary Air-Conditioning Equipment.

        - ARI 270 - Sound Rating of Outdoor Unitary Equipment.

      - ASHRAE (American Society of Heating, Refrigerating and Air Conditioning Engineers)

      - UL (Underwriters Laboratories, Inc.)

  - PERFORMANCE REQUIREMENTS

Select requirements applicable to this Project and edit accordingly. Use for one or identical units. For more units, use Paragraph G with a schedule on the drawings or in the specification.

    - Gas Heating:

      - Input: [___] Btu/hr.

      - Output: [___] Btu/hr.

    - Heat Pump Heating:

      - Rated heating output: [___] Btu/hr.

      - Rated outdoor air temperature: 47 degrees F DB and 43 degrees F, 17 degrees F DB and 15 degrees F.

      - Rated air temperature entering indoor coil: 70 degrees F.

    - Co-efficient of performance: Minimum [___].

    - Cooling Capacity:

      - Rated cooling output: [___] Btu/hr.

      - Air entering evaporator coil: [___] degrees F DB, [___] degrees F.

      - Condenser ambient air: [___] degrees F.

      - Energy efficiency ratio: Minimum [___].

    - Supply Air:

      - Air flow: [___] cfm.

      - External static pressure: [___] inch wg.

    - [Return] [Exhaust] Air:

      - Air flow: [___] cfm.

      - External static pressure: [___] inch wg.

    - Unit Sound Rating: Maximum [___].

Use the following paragraph in conjunction with a Schedule.

    - Scheduled Performance:

      - Cooling capacity: ARI 210, ARI 240 test conditions.

      - Cooling capacity: [___] degrees F condenser ambient air.

      - Heat pump capacity:

      - Rated outdoor air temperature: 47 degrees F DB and 43 degrees F, 17 degrees F DB and 15 degrees F.

      - Rated air temperature entering indoor coil: 70 degrees F.

    - Sound Rating Numbers: ARI 270.

    - Supply and return air: Corrected to [___] feet altitude.

    - Cooling:

      - Cooling capacity: [___] Btu/hr

      - Air flow: [___] cfm.

      - Air entering evaporator: [___] degrees F DB and [___] degrees F WB.

      - Air leaving evaporator: [___] degrees F DB and [___] degrees F WB.

      - Water entering condenser: [___] degrees F.

      - Evaporator fan motor: [___] hp, [___] volts, single or three phase, 60 Hz.

OR

    - Cooling:

      - Cooling capacity: [___] Btu/hr

      - Air flow: [___] cfm.

      - Air entering evaporator: [___] degrees F [___] degrees F DB and [___] degrees F WB.

      - Air leaving evaporator: [___] degrees F DB and [___] degrees F WB.

      - Refrigerant saturated suction temperature: [___] degrees F.

      - Evaporator fan motor: [___] hp, [___] volts, single or three phase, 60 Hz.

    - Air Cooled Units:

      - Cooling capacity at ARI 210 test conditions: [___] Btu/hr with maximum EER of [___] Btu/hr/Watt.

      - Electric resistance heating capacity: [___] Btu/hr.

      - Reverse cycle heating capacity at ARI 240 high and low temperature new test conditions: [___] Btu/hr with COP of [___].

      - ARI 270 sound number: [___].

    - Water Cooled Units:

      - Cooling capacity at ARI 210 test conditions: [___] Btu/hr with maximum EER of [___] Btu/hr.

      - Electric resistance heating capacity: [___] Btu/hr.

      - ARI 270 sound number: [___].

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Submittals shall include the following: Shop Drawings: Indicate capacity and dimensions of manufactured products and assemblies. Indicate electrical service with electrical characteristics and connection requirements, and duct connections.

      - Product Data: Submit data indicating dimensions, rough-in connections, and electrical characteristics and connection requirements. Provide capacity and dimensions of manufactured products and assemblies required for this Project. Indicate electrical service with electrical characteristics and connection requirements, and duct connections. Provide data for manufactured products and assemblies. Indicate water, drain, thermostatic valves, and electrical rough-in connections with electrical characteristics and connection requirements.

      - Manufacturer's Installation Instructions: Submit assembly, support details, connection requirements, and include start-up instructions.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

      - Indicate unit dimensions, weight loading and required clearances.

      - Include equipment schedules: Identification tag, capacities, balancing requirements, weights, etc.

  - QUALITY ASSURANCE

Include the following paragraph only when the costs of acquiring the specified standards are justified.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience, and with service facilities within 100 miles of project.

    - Installer: Company specializing in performing Work of this section with minimum three years documented experience and is approved by manufacturer.

  - DELIVERY, STORAGE, AND HANDLING

    - Accept equipment on site in factory packaging. Inspect for damage.

    - Protect equipment from damage by providing temporary covers until construction is complete in adjacent space. Protect rooftop units from damage by storing off the roof until the roof mounting curbs are in place.

  - MAINTENANCE SERVICE

    - Provide service and maintenance of packaged roof top units for one year from Date of Substantial Completion. Include maintenance items as shown in manufacturer's operating and maintenance data, including filter replacements, fan belt replacement, and controls checkout and adjustments. Provide 24-hour emergency service on breakdowns and malfunctions.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Supply one set of filters fan belts for each unit

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - ROOFTOP AIR CONDITIONING UNITS

    - General

      - Manufacturers: Carrier, Mcquay, Trane, Or Approved Equal.

Edit the following descriptive specifications to identify Project requirements.

      - General: Roof mounted units having [natural propane gas burner] [electric heating elements] and electric refrigeration.

      - Description: Self-contained, packaged, factory assembled and pre-wired, consisting of cabinet and frame, supply fan, [return fan,] [heat exchanger and burner,] [electric heating elements,] [heat recovery coil,] [reversing valve] controls, air filters, refrigerant cooling coil and compressor, condenser coil and condenser fan.

      - The unit shall comply with ARI Standard 210 and shall carry an Underwriters Laboratories, Inc., listing.

    - Fabrication

Omit or select access fastener type.

      - Cabinet: [Steel] [Galvanized steel] with [epoxy resin primer and] baked enamel finish, access doors or removable access panels with quick fasteners [screwdriver operated flush cam type.] [hex-head sheet metal screws] [locking door handle type with piano hinges.]. Structural members shall be minimum 18 gage, with access doors or removable panels of minimum 20 gage.

      - Insulation: [1/2] [one] [2] inch thick [neoprene coated] [aluminum foil] glass fiber with edges protected from erosion.

Select exchanger material.

      - Heat Exchangers: [Aluminized] [Stainless] steel, of welded construction.

Include return air fan if applicable. Some manufacturers do not provide variable pitch pulleys as standard. Use complete isolation in very large units only.

      - Supply [and Return] [and Exhaust] Fan: Forward curved centrifugal type, resiliently mounted with V-belt drive, [adjustable variable pitch motor pulley,] [permanently lubricated bearings], [motor overload protection], and [rubber isolated hinge mounted] [high efficiency] motor [or direct drive as indicated]. [Isolate complete fan assembly.] Refer to Section 20 05 48 - Mechanical Sound, Vibration, and Seismic Control.

      - Air Filters: Easily removed and inspected [35%] [1-inch thick permanent washable.] [1 inch thick glass fiber disposable media in metal frames.] [2 inch thick glass fiber disposable media in metal frames.] [Automatic renewable media with extended surface media filters.] [30%-2” pleated, 85%/90% 10 pocket, 22” bags, charcoal gas phase

      - Roof Mounting Curb: [14] [24] [___] inch high, galvanized steel, channel frame with gaskets, nailer strips [such that supply and return air will be delivered downward].

      - Vibration Isolation Curb: [1/2-inch thick neoprene waffle pad]

    - Burner

      - Gas Burner: [Atmospheric] [Induced draft] [Forced draft] type burner with adjustable combustion air supply, pressure regulator, gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device, and [automatic 100 percent shut-off pilot].

      - Gas Burner Safety Controls: Energize ignition, limit time for establishment of flame, prevent opening of gas valve until [pilot] [burner] flame is proven, stop gas flow on ignition failure, energize blower motor, and after air flow proven and slight delay, allow gas valve to open.

      - High Limit Control: Temperature sensor with fixed stop at maximum permissible setting, de-energize burner on excessive bonnet temperature and energize burner when temperature drops to lower safe value.

      - Supply Fan Control: Temperature sensor sensing bonnet temperatures and independent of burner controls, with provisions for continuous fan operation.

    - Electric Heating Coil

      - [Finned tube heating elements] [or] [Helical nickel-chrome resistance wire coil heating elements with refractory ceramic support bushings] easily accessible with automatic reset thermal cut-out, built-in [magnetic] [mercury] contactors, galvanized steel frame, [control circuit transformer and fuse,] [manual reset thermal cut-out,] [airflow proving device,] [toggle switch (pilot duty),] load fuses.

      - Controls: Start supply fan before electric elements are energized and continue operating until air temperature reaches minimum setting, with switch for continuous fan operation.

    - Evaporator Coil

      - Provide [three row] [seamless] copper tube with [mechanically bonded] aluminum fins coil assembly with galvanized drain pan and piped outlet connection.

      - The coil shall be leak tested at factory to 300 psig.

      - Provide capillary tubes or thermostatic expansion valves for units of 10 tons capacity and less, and thermostatic expansion valves and alternate row circuiting for units 12 tons cooling capacity and larger.

    - Compressor

      - Provide [hermetic] [or] [semi-hermetic] compressors, 3600 rpm maximum, resiliently mounted with positive lubrication, high and low pressure safety controls, motor overload protection, and gage ports.

      - Five-minute timed off circuit to delay compressor start.

      - Outdoor thermostat to energize [compressor above [35] [5] [___] degrees F ambient] [crankcase heater].

Select desired method of capacity control.

      - Provide step capacity control by [hot gas by-pass.] [cycling compressors.] [cylinder unloading.] [cycling multi-speed compressors.]

    - Condenser

      - Provide [three row] [seamless] copper tube with [mechanically bonded] [aluminum] [copper] fin coil assembly [with subcooling rows] [and coil guard].

      - The coil shall be leak tested at factory to 425 psig.

      - Provide direct drive propeller fans, [statically and dynamically balanced] [permanently lubricated bearings] motor overload protection, wired to operate with compressor. [Provide high efficiency fan motors.]

Include pressure switch for operation with low ambient temperatures on all larger units.

      - Provide [refrigerant pressure switches] [outdoor thermostat] to cycle condenser fans.

    - Mixed Air Casing

Select applicable ventilation method.

      - Dampers: Provide manual outside [and return] air dampers for fixed outside air quantity.

OR

      - Dampers: Provide remote controlled outside [and return] air dampers with damper operator and remote rheostat for adjusting outside air quantity.

OR

      - Dampers: Provide outside, return, and relief dampers with damper operator and control package to automatically vary outside air quantity. Outside air damper to fall to closed position. [Relief dampers may be gravity balanced.]

OR

      - The unit shall be equipped with an economizer cycle which shall operate in conjunction with the unit thermostat to use outdoor air for ambient cooling. The economizer shall be equipped with automatically modulated return and outdoor air dampers to maintain proper discharge temperature into conditioned space and shall be equipped with lockout when outdoor temperature is too high for proper cooling. Adjustable minimum position control standard. Spring return damper operators. Gaskets: Provide tight fitting dampers with edge gaskets maximum leakage 5 percent at 2 inches pressure differential.

Select one of the following two paragraphs for the appropriate damper operator.

      - Damper Operator: 24 volt with gear train sealed in oil [with spring return on units 7.5 ton cooling capacity and larger].

OR

      - Damper Operator: Pneumatic piston or gear driven type with spring return [and pilot positioner].

Select control parameter. Select ambient switch over to match particular unit and control sequence.

      - Mixed Air Controls: Maintain selected supply air temperature and return dampers to minimum position on call for heating and above 57 degrees F ambient, above 75 degrees F ambient, when ambient air temperature exceeds return air temperature, when ambient air enthalpy exceeds return air enthalpy.

The following article is typical of controls provided as standard on smaller and single zone units. Some of these features may be provided or required with other control options.

    - Operating Controls

Select applicable controls and controls combination. This article deals with standard, factory available, operating controls for the smaller, single zone units. More sophisticated controls or those for different types of units are contained in later Articles.

      - Provide low voltage, adjustable [room] thermostat to control [burner operation,] [heater stages in sequence with delay between stages,] [compressor and condenser fan,] and supply fan to maintain temperature setting.

        - Include system selector switch [(heat-off-cool)] [(off-heat-auto-cool)] [and fan control switch (auto-on)].

        - Provide double acting thermostat with minimum [___] stage heating and [___] stage cooling.

        - Provide single acting thermostat with minimum [___] stage cooling.

        - Locate thermostat in [room as shown.] [supply air.] [return air.]

OR

      - Provide terminal strip on unit for connection of operating controls to remote panel. Provide control for [two] [___] stages of heating and [two] [___] stages cooling.

      - Provide remote mounted fan control switch (on-auto).

      - Provide low limit thermostat in supply air to close outside air damper and] stop supply fan.

      - Provide night control energized by central time clock to [maintain lower thermostat setting,] [maintain night thermostat setting,] [lock out refrigeration,] [close outside air damper and open return air damper,] [stop supply air fan,] [set fan control switch to auto position,] for night and unoccupied operation. [Provide time delay to maintain outside air damper closed and return air damper to open position after switching to day and occupied operation.]

Select applicable panel options. Generally options are not standard but available.

      - Provide remote readout panels containing signal lights indicating system status, [heating system failure,] [cooling system failure,] and dirty filters; check switches proving signal light operations; system on-off switch [,] [and cooling system on-off switch].

Select panel options to match operating controls.

      - Provide in panel a [manual 12 hour timer to override night control,] [7 day time clock for energizing night control,] [remote damper control,] [low limit manual reset,] [and] [remote thermostat temperature set point].

    - Operating Controls - Single Zone Units

      - Electric solid state microcomputer based room thermostat, [located as indicated in service area with remote sensor] located as indicated.

      - Room thermostat shall incorporate:

        - Automatic switching from heating to cooling.

        - Preferential rate control to minimize overshoot and deviation from set point.

        - Set-up for four separate temperatures per day.

        - Instant override of set point for continuous or timed period from one hour to 31 days.

        - Short cycle protection.

        - Programming based on weekdays, Saturday and Sunday.

        - Switch selection features including imperial or metric display, 12 or 24-hour clock, keyboard disable, remote sensor and fan-on-auto.

      - Room thermostat display shall include:

        - Time of day.

        - Actual room temperature.

        - Programmed temperature.

        - Programmed time.

        - Duration of timed override.

        - Day of week.

        - System model indication: heating, cooling, auto, off, fan auto, fan on.

        - Stage (heating or cooling) operation.

      - Provide low limit thermostat in supply air to close outside air dampers and stop supply fan.

    - Operating Controls - Variable Volume Units

      - Local temperature transmitter in supply air to signal electronic logic panel to control mixing dampers and cooling in sequence. Operate mixing section as first stage of cooling and revert to minimum outside air above approximately 75 degrees F as determined by [enthalpy] [temperature] of return and outdoor air.

      - Control cooling by cycling compressors, cylinder unloading, and hot gas bypass.

      - Control logic to allow supply air reset under low load or airflow conditions.

      - Provide seven-day time clock with spring carry over (or electronic clock with battery backup) to control unit on occupied/un-occupied schedule. At night, unit shall be off. Locate clock in remote control panel with status lights.

      - Provide two-stage morning warm-up thermostat to hold outdoor dampers closed and energize heat until return air temperature reaches set point.

      - Provide [within roof curb,] by-pass dampers, bypassing air from supply fan discharge to return fan inlet to control duct static pressures. Control operation by sensing current to supply fan motor.

    - Heat Recovery Coil

      - Provide copper tube aluminum fin coil assembly [with multiple circuits] arranged to provide heat recovery.

      - Heating Capacity:

        - Heating output: [___] Btu/hr.

        - Air entering coil: [___] degrees F.

        - Air leaving coil: [___] degrees F.

Select the appropriate heat recovery medium.

      - Condensing temperature: [___] degrees F.

OR

      - Water:

        - Temperature entering coil: [___] degrees F.

        - Temperature leaving coil: [___] degrees F.

        - Water flow: [___] gpm.

  - PACKAGED AIR CONDITIONING UNITS

    - General

      - Manufacturers: Carrier, Mcquay, Trane, Or Approved Equal.

Edit the following descriptive specifications to identify Project requirements.

      - Packaged, self-contained, factory assembled, pre-wired unit, consisting of cabinet, compressor, condensing coil, evaporator fan, evaporator coil, [discharge plenum,] [outside air connection,] [heating coil,] air filters, and controls; fully charged with refrigerant and filled with oil.

      - Assembly: [Up flow] [Horizontal flow] air delivery, in draw-through configuration as indicated.

      - The unit shall comply with ARI Standard 210 and shall carry an Underwriters Laboratories, Inc., listing.

    - Cabinet

      - Frame and Panels: Galvanized steel with [epoxy resin primer and] baked enamel finish, easily removed access-doors or panels.

      - Insulation: Minimum 1/2-inch thick acoustic duct liner for lining cabinet interior.

      - Drain Pan: Galvanized steel with corrosion-resistant coating or molded corrosion-resistant material.

    - Evaporator Fan

      - Fan: [V-Belt driven, with permanently lubricated bearings] [Direct drive], [double width, double inlet, forward curved centrifugal] [propeller] fan, statically and dynamically balanced, resiliently mounted.

      - V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed. Variable and adjustable pitch motor sheave selected so required rpm is obtained with sheaves set at mid-position as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor. [Guard to have tachometer opening

      - Motors: [___] hp[with motor overload protection]

    - Heating Coil

      - [Hot water] [Steam] heating copper tube coil with tubes expanded into aluminum fins.

OR

      - Helical nickel-chrome resistance wire coil heating elements with refractory ceramic support bushings, with automatic reset thermal cutout, built-in magnetic contactors, manual reset thermal cut-out, airflow proving device, load fuses.

    - Evaporator Coil

      - Direct expansion coil of [three row] [seamless] copper [or aluminum] tubes expanded into [mechanically bonded] aluminum fins.

      - Refrigeration circuit with expansion device, [filter-drier], and charging valves.

      - The coil shall be leak tested at factory to 300 psig.

    - Compressor

      - Hermetically sealed, 3600 rpm maximum resiliently mounted with positive lubrication and internal motor protection.

    - Condenser

There are three condenser options: water cooled condenser, remote mounted air-cooled condenser, and integral air-cooled condenser. Edit accordingly.

      - Co-Axial, copper tube in copper tube or shell and tube with [finned] copper tubes in steel shell with water temperature actuated water-regulating valve.

OR

      - Terminating suction and liquid refrigerant piping with service valves within unit.

OR

      - Fan: Statically and dynamically balanced, with permanently lubricated bearings. Provide direct drive propeller fans, motor overload protection, wired to operate with compressor.

      - V-Belt Drive: Dynamically balanced, bored to fit shafts and keyed. Variable and adjustable pitch motor sheave selected so required rpm is obtained with sheaves set at mid-position as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor.

      - Motors: [___] hp

    - Air Filters

Select desired filters.

      - Easily removed and inspected, ASHRAE 35%] [one inch thick permanent cleanable] [2 inch thick disposable glass fiber] panel filters.]

      - ASHRAE 30% - 2" pleated, 85%/90% 10pocket 22" bags, Charcoal Gas Phase.  Provide three complete sets of filters: One for use during construction, one initial operating set, and one replacement set to be turned over to the owner at time of occupancy.

    - Controls

      - Factory wired controls shall include [contactor], [high and low pressure cutouts], [internal winding thermostat for compressor], [control circuit transformer], [non-cycling reset relay.]

      - Provide thermostat to cycle cooling within unit with 'fan-off-cool' switch allowing continuous fan operation, or cycling fan on call for cooling.

OR

      - Provide room thermostat to control cooling with 'cool-off' selector switch and 'auto-on' fan control switch.

OR

      - Provide low voltage, adjustable [room] thermostat to control [heater stages in sequence with delay between stages,] compressor, [condenser,] and supply fan to maintain temperature setting. Include system selector switch [(heat-off-cool)] [(off-heat-auto-cool)] [and fan control switch (auto-on)].

Use the following paragraph for more detailed controls and when heating coils are provided.

      - Refer to Section 23 09 23 - Direct Digital Controls.

OR

      - Cooling:

        - Cooling capacity: [___] Btu/hr

        - Evaporator airflow: [___] cfm.

        - Air entering evaporator: [___] degrees F DB and [___] degrees F WB.

        - Air leaving evaporator: [___] degrees F DB and [___] degrees F WB.

        - Condenser airflow: [___] cfm.

        - Air entering condenser: [___] degrees F.

        - Evaporator fan motor: [___] hp, [___] volts, [single] [three] phase, 60 Hz.

        - Condenser fan motor: [___] hp, [___] volts, [single] [three] phase, 60 Hz.

      - Heating:

        - Heating capacity: [___] Btu/hr.

        - Water flow: [___] gpm.

        - Water entering [___] degrees F.

        - Water leaving: [___] degrees F.

OR

      - Heating:

        - Heating capacity: [___] Btu/hr.

        - Steam flow: [___] lb./hr.

        - Steam pressure: [___] psig.

OR

      - Heating:

        - Electric resistance heating capacity: [___] Btu/hr.

    - Electrical Characteristics And Components

Select one or more of the following subparagraphs appropriate to the equipment requirements.

      - Section 26 27 26 - Wiring Devices: Requirements for electrical characteristics.

        - [___] hp. [[___] rated load amperes.]

        - [___] volts, [single] [three] phase, 60 Hz.

        - [___] amperes maximum [fuse size] [circuit breaker size] [overcurrent protection].

        - [___] minimum circuit ampacity.

        - [___] percent minimum power factor at rated load.

      - Division 26 Electrical: Requirements for motors.

      - Disconnect Switch: Factory mount [in control panel] [on equipment].

  - TERMINAL AIR CONDITIONING UNITS

    - General

Edit the following descriptive specifications to identify Project requirements. Select appropriate options as required for this Project.

      - Description: Packaged, self-contained, through-the-wall [air] [water] cooled terminal [air conditioning] units, with [wall sleeve,] room cabinet, electric refrigeration system, [electric] [hot water] [steam] [gas fired] heating, [outside air louvers,] [built-in] [remote] temperature controls; fully charged with refrigerant and filled with oil.

    - Cabinet

Select appropriate mounting arrangement.

      - Cabinet: [Wall mounted] [Floor mounted] [Sub-base mounted] of [18 gage] galvanized steel with [epoxy coated] [baked enamel] finish, removable front panel with concealed latches, [___] color [as selected].

      - Discharge Grille and Access Door: [Removable] [Integral] [punched louver] [extruded aluminum] discharge grilles [,] [allowing 4-way discharge air pattern,] with hinged door in top of cabinet for access to controls.

      - Wall Cabinet: Matching cabinet in construction and finish, allowing diversion of [40] [___] percent of unit air flow to adjoining room, with grille.

    - Wall Sleeves And Louvers

Insert requirements. Use this paragraph for one or identical units. When specifying units of differing sizes, use a schedule.

      - Wall Sleeves: [___] inches deep, [16 gage] galvanized steel with [protective mastic coating] [polyester finish].

      - Louvers: [Flush] [Companion flanged] [anodized] aluminum [with enamel finish], [___] color [as selected].

    - Chassis

Select appropriate components. The accumulator, expansion valve, and reversing valve are generally only required in heat pump units.

      - Refrigeration System:

        - Direct expansion [cooling] [indoor] coil.

        - Hermetically sealed compressor with internal spring isolation, external isolation, permanent split capacitor motor and overload protection.

        - Accumulator.

        - [Condenser] [Outdoor] coil and fan.

OR

        - Coaxial tube-in-tube condenser with water- regulating valve.

        - Capillary restrictor [and constant pressure expansion valve].

        - Reversing valve.

      - Air System: Centrifugal forward curved [tangential] [evaporator] [indoor] fans with [two speed] permanent split capacitor motor, permanent washable filters, positive pressure ventilation damper with concealed manual operator.

      - Heating Coil: [Electric.] [Hot water.] [Steam.]

      - Condensate Drain: Drain pan to direct condensate to [condenser] [outdoor] coil for re-evaporation.

      - [Condenser] [Outdoor] Fan: [Centrifugal, forward curved] [Propeller] type [with separate permanent split capacitor motor.] [driven by [evaporator] [indoor] fan motor.]

    - Controls

Select applicable control options.

      - Control Module: [Unit] [Remote] mounted adjustable thermostat with heat anticipator, [heat-off-cool] [off-heat-auto-cool] switch, [high-low] fan switch.

      - Low Ambient Lockout Control: Below [35] [___] degrees F, outdoor thermostat shall [prevent compressor operation] [and switch to heat mode].

    - Electrical Characteristics And Components

Select one or more of the following subparagraphs appropriate to the equipment requirements.

      - [[___] hp] [[___] rated load amperes.]

      - [___] volts, [single] [three] phase, 60 Hz.

      - [___] amperes maximum [fuse size] [circuit breaker size] [overcurrent protection].

      - [___] minimum circuit ampacity.

      - [___] percent minimum power factor at rated load.

      - Division 26 Electrical: Requirements for motors.

      - Disconnect Switch: Factory mount [in control panel] [on equipment].

- EXECUTION

  - PREPARATORY WORK

    - Section 01 31 13 - Project Coordination: Coordination and project conditions.

    - Inspection: Prior to all Work of this section, carefully inspect the Work of all other trades and verify that all such Work is complete to the point where this Work may properly commence.

    - Verify that roof curbs are installed and dimensions are as [shown on shop drawings] [instructed by the manufacturer].

    - Discrepancies: In the event of a discrepancy, do not proceed with the Work in dispute until all such discrepancies have been resolved by the Engineer.

    - Notification: Notify the proper agency and receive sign-off inspection when required before proceeding with the Work.

  - INSTALLATION

    - Mount rooftop units on factory built roof-mounting curb providing watertight enclosure to protect ductwork and utility services. Install roof mounting curb level.

    - Install all equipment in accordance with the manufacturer’s recommendations.

    - Locate remote panels [where indicated] [___].

    - Connect controls to remote locations.

    - Mount indoor units on vibration isolators.

    - Connect indoor units to supply and return ductwork with flexible connections.

    - Provide shut-off valves in condenser water inlet and outlet piping.

    - Pipe refrigerant from unit to condenser.

    - Pipe condensate from drain pan to [nearest floor drain] [condensate drainage system] [___].

    - On water coils, provide shut-off valve on supply line and [balancing valve] [flow control and shut-off valve] on return line. Provide [manual] [float operated automatic] air vents at high points complete with stop valve.

    - In steam coils, provide shut-off valve and vacuum breaker in steam line. Install steam traps with outlet below coil return connection.

  - MANUFACTURER'S FIELD SERVICES

    - Section 01 45 16.13 - Contractor’s Quality Control Program: Manufacturers’ field services.

    - Provide initial start-up and shutdown during first year of operation, including routine servicing and checkout.

  - DEMONSTRATION AND TRAINING

    - Demonstrate unit operation and maintenance.

  - TESTS

    - Prior to final inspection of the Work in this section, perform all required tests and obtain all required approvals of regulatory agencies.

    - Should the results of a test indicate an improperly functioning system, correct the problem to the satisfaction of the Engineer at no additional cost to the Port.

  - MANUALS

    - Prepare and furnish operation and maintenance manuals.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Sole Source