READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

Division 23 Section 23 81 43 Heat Pumps is not for use at Airport.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Heat Pumps” Work is shown in the Contract Documents. Section includes packaged rooftop heat pumps and controls, roof mounting curb and base, unitary heat pumps and controls, and packaged terminal heat pump units and controls.

  - GOVERNING CODES, STANDARDS AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - ARI (Air Conditioning and Refrigeration Institute)

        - ARI 210 - Unitary Air-Conditioning Equipment.

        - ARI 240 - Air Source Unitary Heat Pump Equipment.

        - ARI 270 - Sound Rating of Outdoor Unitary Equipment.

        - ARI 340 – Commercial and Industrial Unitary Heat Pump Equipment.

      - NEMA (National Electrical Manufacturers Association)

      - Port of Seattle Standards

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions.

    - Submittals shall include the following:

      - Shop Drawings: Indicate capacity and dimensions of manufactured products and assemblies. Indicate electrical service with electrical characteristics and connection requirements, and duct connections.

      - Product Data: Submit drawings indicating dimensions, rough-in connections, and electrical characteristics and connection requirements. Provide capacity and dimensions of manufactured products and assemblies required for this project. Indicate electrical service with electrical characteristics and connection requirements, and duct connections. Provide data for manufactured products and assemblies. Indicate glycol, drain, thermostatic valves, and electrical rough-in connections with electrical characteristics and connection requirements.

      - Schedule: Include product schedule with identification tags.

      - Manufacturer's Installation Instructions: Submit assembly, support details, clearance requirements, seismic requirements, connection requirements, and include start-up instructions.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

  - PERFORMANCE REQUIREMENTS - ROOF TOP HEAT PUMPS

Select requirements applicable to this Project and edit accordingly. Use for one or identical units.

    - Heat Pump Heating:

      - Rated heating output: [___] Btu/hr.

      - Rated outdoor air temperature: 47 degrees F DB and 43 degrees F WB, 17 degrees F DB and 15 degrees F WB.

      - Rated air temperature entering indoor coil: 70 degrees F.

    - Co-efficient of performance: Minimum [___].

    - Heat Pump Cooling Capacity:

      - Rated cooling output: [___] Btu/hr.

      - Air entering evaporator coil: [___] degrees F DB, [___] degrees F WB.

      - Condenser ambient air: [___] degrees F.

      - Energy efficiency ratio: Minimum [___].

    - Supply Air:

      - Air flow: [___] cfm.

      - External static pressure: [___] inch wg.

    - [Return] [Exhaust] Air:

      - Air flow: [___] cfm.

      - External static pressure: [___] inch wg.

    - Unit Sound Rating: Maximum [___].[35 db] at casing surface]

Use the following paragraph in conjunction with a Schedule for non-identical units.

    - Scheduled Performance:

      - Cooling capacity: ARI 240 test conditions.

      - Cooling capacity: [___] degrees F condenser ambient air.

      - Heat pump capacity:

      - Rated outdoor air temperature: 47 degrees F DB and 43 degrees F WB, 17 degrees F DB and 15 degrees F WB.

      - Rated air temperature entering indoor coil: 70 degrees F.

    - Sound Rating Numbers: ARI 270.

    - Supply and return air: Corrected to [___] feet altitude.

  - PERFORMANCE REQUIREMENTS - UNITARY HEAT PUMP UNITS

Insert performance requirements. Use this paragraph for one or identical units. Use the schedule at the end of this section or on the drawings when specifying units of different sizes.

    - Cooling:

      - Cooling capacity: [___] Btu/hr

      - Air flow: [___] cfm.

      - Air entering evaporator: [___] degrees F DB and [___] degrees F WB.

      - Air leaving evaporator: [___] degrees F DB and [___] degrees F WB.

      - Water entering condenser: [___] degrees F.

      - Evaporator fan motor: [___] hp, [___] volts, [single] [three] phase, 60 Hz.

OR

    - Cooling:

      - Cooling capacity: [___] Btu/hr

      - Air flow: [___] cfm.

      - Air entering evaporator: [___] degrees F DB and [___] degrees F WB.

      - Air leaving evaporator: [___] degrees F DB and [___] degrees F WB.

      - Refrigerant saturated suction temperature: [___] degrees F.

      - Evaporator fan motor: [___] hp, [___] volts, single or three phase, 60 Hz.

OR

    - Cooling:

      - Cooling capacity: [___] Btu/hr

      - Evaporator airflow: [___] cfm.

      - Air entering evaporator: [___] degrees F DB and [___] degrees F WB.

      - Air leaving evaporator: [___] degrees F DB and [___] degrees F WB.

      - Condenser airflow: [___] cfm.

      - Air entering condenser: [___] degrees F.

      - Evaporator fan motor: [___] hp, [___] volts, single or three phase, 60 Hz.

      - Condenser fan motor: [___] hp, [___] volts, single or three phase, 60 Hz.

    - Heating:

      - Electric resistance heating capacity: [___] Btu/hr.

  - PERFORMANCE REQUIREMENTS - PACKAGED TERMINAL HEAT PUMP UNITS

Insert requirements. Use this article for one or identical units. When specifying units of differing sizes, use a schedule.

    - Air Cooled Units:

      - Cooling capacity at ARI 210 test conditions: [___] with maximum EER of [___] Btu/hr/Watt.

      - Electric resistance heating capacity: [___] Btu/hr/Watt.

      - Heat pump heating capacity at ARI 240 high and low temperature new test conditions: [___] Btu/hr with COP of [___].

      - ARI 270 sound number: [___].

    - Water Cooled Units:

      - Cooling capacity at ARI 210 test conditions: [___] Btu/hr with maximum EER of [___] Btu/hr/Watt.

      - Electric resistance heating capacity: [___] Btu/hr.

      - Heat pump heating capacity at ARI 240 [high] [low] temperature new test conditions: [___] Btu/hr with COP of [___], [___] gpm condenser water entering at [___] degrees F.

      - ARI 270 sound number: [___].

    - Scheduled performance:

      - Cooling capacity: ARI 210.

      - Heat pump heating capacity: ARI 240.

      - Unit, sound number: ARI 270.

  - QUALITY ASSURANCE

    - Provide materials in accordance Port of Seattle standards.

Include the following paragraph only when the costs of acquiring the specified standards are justified.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience, and with service facilities within 100 miles of Project.

    - Installer: Company specializing in performing Work of this section with minimum three years documented experience approved by manufacturer.

  - DELIVERY, STORAGE, AND HANDLING

    - Accept heat pump units on site in factory packaging. Inspect for damage.

    - Protect terminal heat pump units from damage by providing temporary covers until construction is complete in adjacent space. Protect rooftop heat pump units from damage by storing off the roof until the roof mounting curbs are in place.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

  - MAINTENANCE SERVICE

    - Provide service and maintenance of packaged heat pump roof top units for one year from Date of Substantial Completion. Include maintenance items as shown in manufacturer's operating and maintenance data, including filter replacements, fan belt replacement, and controls checkout and adjustments. Provide 24-hour emergency service on breakdowns and malfunctions.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Supply one set of filters and fan belts for each unit

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - ROOFTOP HEAT PUMPS

    - Manufacturers: Carrier, Trane, Or Approved Equal.

Define what would constitute an equal product.

Edit the following descriptive specifications to identify Project requirements.

    - General: Roof mounted units having supplementary electric heating elements and electric refrigeration.

    - Description: Self-contained, packaged, factory assembled and pre-wired, consisting of cabinet and frame, supply fan, return fan, electric heating elements, reversing valve, controls, air filters, compressor, refrigerant coils and fans.

    - Electrical Characteristics:

    - [___] kW] [___] rated load amperes.

    - [___] volts, single or three phase, 60 Hz [___] minimum circuit ampacity.

    - [___] amperes maximum fuse size, circuit breaker size and overcurrent protection.

    - Refer to Division 26 Electrical.

    - Disconnect Switch: Factory or field mount in control panel and on equipment under provisions of Division 26 Electrical.

  - FABRICATION

Omit or select access fastener type.

    - Cabinet: Steel or galvanized steel with baked enamel finish, access doors or removable access panels with quick fasteners, screwdriver operated flush cam type, hex-head sheet metal screws or locking door handle type with piano hinges. Provide minimum 18 gage structural members, with access doors or removable panels of minimum 20 gage.

    - Insulation: ½, 1, 2 inch thick neoprene coated aluminum foil, glass fiber with edges protected from erosion.

Include return air fan if applicable. Some manufacturers do not provide variable pitch pulleys as standard. Use complete isolation in very large units only.

    - Supply, Return and Exhaust Fans: Forward curved centrifugal type, resiliently mounted with V-belt drive, adjustable variable pitch motor pulley, and rubber isolated hinge mounted high efficiency motor or direct drive as indicated. Isolate complete fan assembly. Refer to Section 20 05 48 - Mechanical Sound, Vibration, and Seismic Control.

    - Air Filters: 1-inch thick permanent washable. 1 inch thick glass fiber disposable media in metal frames. 2 inch thick glass fiber disposable media in metal frames. Automatic renewable media with extended surface media filters.

    - Roof Mounting Curb: 14 to 24 inches high, galvanized steel, channel frame with gaskets, nailer strips.

  - ELECTRIC HEATING COIL

    - Finned tube heating elements or helical nickel-chrome resistance wire coil heating elements with refractory ceramic support bushings, easily accessible with automatic reset thermal cut-out, built-in magnetic mercury contactors, galvanized steel frame, control circuit transformer and fuse, manual reset thermal cut-out, airflow proving device, toggle switch (pilot duty), load fuses.

    - Controls: Ensure supply fan is operating before electric elements are energized. Operate electric heater in 2 or 3 stages when outdoor ambient is too low to maintain space thermostat setting with compressor operation.

  - SPACE SUPPLY AIR COIL

    - Provide copper tube aluminum fin coil assembly with galvanized drain pan and connection.

    - Provide capillary tubes or thermostatic expansion valves for units of 10 tons capacity and less, and thermostatic expansion valves and alternate row circuiting for units 12 tons cooling capacity and larger.

  - COMPRESSOR

    - Provide hermetic or semi-hermetic compressors, 3600 rpm maximum, resiliently mounted with positive lubrication, high and low pressure safety controls, motor overload protection, and gage ports.

    - Five-minute timed off circuit to delay compressor start.

    - Outdoor thermostat to energize compressor above 35 degrees F ambient.

Select desired method of capacity control.

    - Provide step capacity control by hot gas by-pass, cycling compressors, cylinder unloading and cycling multi-speed compressors.

    - Provide reversing valve, suction line accumulator, discharge muffler, flow control check valve, and solid-state defrost control.

  - OUTDOOR COIL

    - Provide copper tube aluminum or copper fin coil assembly with sub cooling rows and coil guard.

    - Provide direct drive propeller fans, motor overload protection, wired to operate with compressor. Provide high efficiency fan motors.

Include pressure switch for operation with low ambient temperatures on all larger units.

    - Provide refrigerant pressure switches and an outdoor thermostat to cycle fans.

  - MIXED AIR CASING

Select applicable ventilation method. The third option, a complete economizer, includes Paragraphs A through D.

    - Dampers: Provide manual outside and return air dampers for fixed outside air quantity.

OR

    - Dampers: Provide remote controlled outside and return air dampers with damper operator and remote rheostat for adjusting outside air quantity.

OR

    - Dampers: Provide outside, return and relief dampers with damper operator and control package to automatically vary outside air quantity. Outside air damper to fall to closed position. Relief dampers may be gravity balanced.

    - Gaskets: Provide tight fitting dampers with edge gaskets, maximum leakage 5 percent at 2 inches pressure differential.

Select one of the following two paragraphs for the appropriate damper operator.

    - Damper Operator: 24 volt with gear train sealed in oil with spring return on units 7.5 ton cooling capacity and larger.

OR

    - Damper Operator: Pneumatic piston or gear driven type with spring return and pilot positioner.

Select control parameter. Select ambient switch over to match particular unit and control sequence.

    - Mixed Air Controls: Maintain selected supply air temperature and return dampers to minimum position on call for heating and above 57 degrees F ambient, above 75 degrees F ambient, when ambient air temperature exceeds return air temperature, when ambient air enthalpy exceeds return air enthalpy.

The following article is typical of controls provided as standard on smaller and single zone units. Some of these features may be provided or required with other control options.

  - OPERATING CONTROLS - SINGLE ZONE UNITS

    - Electric solid state microcomputer based room thermostat, located as indicated in service area with remote sensor located as indicated.

    - Room thermostat shall incorporate:

      - Automatic switching from cooling to heat pump heating to supplemental electric heating.

      - Instant override of set point for continuous or timed period from one hour to 31 days.

      - Short cycle protection.

      - Programming based on weekdays, Saturday and Sunday.

      - Switch selection features including imperial or metric display, 12 or 24-hour clock, keyboard disable, remote sensor and fan-on-auto.

    - Room thermostat display shall include:

      - Time of day.

      - Actual room temperature.

      - Programmed temperature.

      - Programmed time.

      - Duration of timed override.

      - Day of week.

      - System model indication: cooling, heating, supplemental heating, auto, off, fan auto, fan on.

      - Stage (heating or cooling) operation.

    - Provide low limit thermostat in supply air to close outside air dampers and stop supply fan.

  - OPERATING CONTROLS

Select applicable controls and controls combination. This article deals with standard, factory available, operating controls for the smaller, single zone units. More sophisticated controls or those for different types of units are contained in articles following.

    - Provide low voltage, adjustable room thermostat to control heater stages in sequence with delay between stages, compressor and outdoor coil fan supply fan to maintain temperature setting.

      - Include system selector switch heat-off-cool, off-heat-auto-cool and fan control switch (auto-on).

      - Provide double acting thermostat with minimum [___] stage heating and [___] stage cooling.

      - Provide single acting thermostat with minimum [___] stage cooling.

      - Locate thermostat in room as shown. Supply air, Return air.

OR

    - Provide terminal strip on unit for connection of operating controls to remote panel. Provide control for two stages of heating and two stages cooling.

    - Provide remote mounted fan control switch (on-auto).

    - Provide low limit thermostat in supply air to close outside air damper and stop supply fan.

    - Provide night control energized by central time clock to lock out refrigeration, close outside air damper and open return air damper, stop supply air fan, set fan control switch to auto position, for night and unoccupied operation. Provide time delay to maintain outside air damper closed and return air damper to open position after switching to day and occupied operation.

Select applicable panel options. Generally options are not standard but available.

    - Provide remote readout panels containing signal lights indicating system status, system failure and dirty filters; check switches proving signal light operations; system on-off switch.

Select panel options to match operating controls.

    - Provide in panel a manual 12 hour timer to override night control, 7 day time clock for energizing night control, remote damper control, low limit manual reset, and remote thermostat temperature set point.

  - OPERATING CONTROLS - VARIABLE VOLUME UNITS

    - Temperature transmitter located in supply air to signal electronic logic panel to control mixing dampers and cooling in sequence. Operate mixing section as first stage of cooling and revert to minimum outside air above approximately 75 degrees F as determined by enthalpy, temperature of return and outdoor air.

    - Control cooling by cycling compressors, cylinder unloading, and hot gas bypass.

    - Provide control logic to allow supply air reset under low load or airflow conditions.

    - Provide seven-day time clock with spring carry over (or electronic clock with battery backup) to control unit on occupied/un-occupied schedule. At night, unit shall be off. Locate clock in remote control panel with status lights.

    - Provide two-stage morning warm-up thermostat to hold outdoor dampers closed and energize heat until return air temperature reaches set point.

    - Provide within roof curb, by-pass dampers, bypassing air from supply fan discharge to return fan inlet to control duct static pressures. Control operation by sensing current to supply fan motor.

  - UNITARY HEAT PUMP UNITS

    - Manufacturers: Carrier, Trane, Or Approved Equal.

Define what would constitute an equal product.

Edit the following descriptive specifications to identify Project requirements.

    - Packaged, self-contained, factory assembled, pre-wired unit, consisting of cabinet, compressor, condensing coil, evaporator fan, evaporator coil, discharge plenum, outside air connection, heating coil, air filters, and controls; fully charged with refrigerant and filled with oil.

    - Assembly: Up flow, horizontal flow air delivery, in draw-through configuration as indicated.

    - Electrical Characteristics:

      - [___] rated load amperes.

      - [___] volts, single or three phase, 60 Hz.

      - [___] amperes maximum fuse size, circuit breaker size and overcurrent protection.

      - Refer to Division 26 Electrical.

      - Disconnect Switch: Factory mount in control panel and on equipment under provisions of Division 26 Electrical.

  - CABINET

    - Frame and Panels: Galvanized steel with baked enamel finish, easily removed access-doors or panels.

    - Insulation: Minimum 1/2-inch thick acoustic duct liner for lining cabinet interior.

    - Drain Pan: Galvanized steel with corrosion-resistant coating or molded corrosion-resistant material.

  - SUPPLY AIR FAN

    - Fan: V-Belt driven, with permanently lubricated bearings direct drive, double width, double inlet, forward curved centrifugal propeller fan, statically and dynamically balanced, resiliently mounted.

    - V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shafts and keyed. Variable and adjustable pitch motor sheave selected so required rpm is obtained with sheaves set at mid-position as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor.

    - Motors: [___] hp, [___] volts, single or three phase, 60 Hz; multi-speed PSC type refer to Division 26 Electrical , NEMA MG1 and [___].

  - COMPRESSOR

    - Hermetically sealed, 3600 rpm maximum resiliently mounted with positive lubrication and internal motor protection.

  - SUPPLY AIR COIL

    - Direct expansion coiling coil of copper or aluminum tubes expanded into aluminum fins.

    - Refrigeration circuit with expansion device, filter-drier, and charging valves.

  - CONDENSER

There are three condenser options: water cooled condenser, remote mounted air-cooled condenser, and integral air-cooled condenser. Edit accordingly.

    - Co-Axial, copper tube in copper tube or shell and tube with finned copper tubes in steel shell with water temperature actuated water-regulating valve.

OR

    - Terminating suction and liquid refrigerant piping with service valves within unit.

OR

    - Fan: Statically and dynamically balanced, with permanently lubricated bearings.

    - V-Belt Drive: Dynamically balanced, bored to fit shafts and keyed. Variable and adjustable pitch motor sheave selected so required rpm is obtained with sheaves set at mid-position as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor.

    - Motors: [___] hp, [___] volts, single or three phase, 60 Hz, refer to Division 26 Electrical, to NEMA MG1 and [___].

  - HEATING COIL

    - Helical nickel-chrome resistance wire coil heating elements with refractory ceramic support bushings, with automatic reset thermal cut-out, built-in magnetic contactors, manual reset thermal cut-out, airflow proving device and load fuses.

  - AIR FILTERS

Select desired filters.

    - Easily removed one inch thick permanent cleanable or 2 inch thick disposable glass fiber panel filters.

  - CONTROLS

    - Factory wired controls shall include contactor, high and low pressure cutouts, internal winding thermostat for compressor, control circuit transformer and non-cycling reset relay.

    - Provide thermostat to cycle cooling within unit with 'fan-off-cool' switch allowing continuous fan operation, or cycling fan on call for cooling.

OR

    - Provide room thermostat to control cooling with 'cool-off' selector switch and 'auto-on' fan control switch.

OR

    - Provide low voltage, adjustable room thermostat to control heater stages in sequence with delay between stages, compressor, condenser, and supply fan to maintain temperature setting. Include system selector switch (heat-off-cool), (off-heat-auto-cool) and fan control switch (auto-on).

Use the following paragraph for more detailed controls.

    - Refer to Section 23 09 23 - Direct Digital Controls.

  - PACKAGED TERMINAL HEAT PUMP UNITS

    - Provide materials in accordance Port of Seattle standards.

Edit the following descriptive specifications to identify Project requirements. Select appropriate options as required for this Project.

    - Description: Packaged, self-contained, through-the-wall air or water  source terminal heat pump units, with wall sleeve, room cabinet, electric refrigeration system, electric heating, outside air louvers, built-in remote temperature controls; fully charged with refrigerant and filled with oil.

    - Electrical Characteristics:

      - [___] rated load amperes.

      - [___] volts, single or three phase, 60 Hz.

      - [___] amperes maximum fuse size, circuit breaker size and overcurrent protection.

      - Refer to Division 26 Electrical.

      - Disconnect Switch: Factory mount on equipment under provisions of Division 26 Electrical.

  - CABINET

Select appropriate mounting arrangement.

    - Cabinet: Wall mounted, Floor mounted, Sub-base mounted of 18 gage galvanized steel with epoxy coated baked enamel finish, removable front panel with concealed latches and color as selected.

    - Where conditioner is indicated to be ceiling hung, the conditioner manufacturer shall provide a kit of four hanger bracket assemblies, comprising a heavy steel hanger bracket, integral vibration isolator, cap screw and plated isolator washer. Hanger bracket assembly shall accommodate a 3/8" maximum diameter hanger rod. No external channel or angle trapeze assemblies under conditioner will be allowed.

    - Discharge Grille and Access Door: Removable, integral, punched louver, extruded aluminum discharge grilles, allowing 4-way discharge air pattern, with hinged door in top of cabinet for access to controls.

    - Wall Cabinet: Matching cabinet in construction and finish, allowing diversion of 40 percent of unit air flow to adjoining room, with grille.

  - WALL SLEEVES AND LOUVERS

Insert requirements. Use this paragraph for one or identical units. When specifying units of differing sizes, use a schedule.

    - Wall Sleeves: [___] inches deep, 16 gage galvanized steel with protective mastic coating, polyester finish.

    - Louvers: Flush, companion flanged anodized aluminum with enamel finish and color as selected.

  - CHASSIS

Select appropriate components.

    - Refrigeration System:

      - Direct expansion indoor coil.

      - Hermetically sealed compressor with internal spring isolation, external isolation, permanent split capacitor motor and overload protection.

      - Accumulator.

      - Outdoor coil and fan.

OR

      - Coaxial tube-in-tube condenser with water- regulating valve.

      - Capillary restrictor and constant pressure expansion valve.

      - Reversing valve.

    - Air System: Centrifugal forward curved tangential indoor fans with two speed permanent split capacitor motor, permanent washable filters, positive pressure ventilation damper with concealed manual operator.

    - Heating Coil: Electric.

    - Condensate Drain: Drain pan to direct condensate to outdoor coil for re-evaporation.

    - Outdoor Fan: Centrifugal, forward curved or propeller type with separate permanent split capacitor motor driven by evaporator indoor fan motor.

  - CONTROLS

Select applicable control options.

    - Control Module: Unit, Remote mounted adjustable thermostat with heat anticipator, heat-off-cool, off-heat-auto-cool, switch, with high-low fan switch.

    - Low Ambient Lockout Control: Below 35 degrees F, outdoor thermostat shall prevent compressor operation and switch to supplemental heat mode.

  - ELECTRICAL CHARACTERISTICS AND COMPONENTS

Select one or more of the following subparagraphs appropriate to the equipment requirements.

    - Section 26 27 26 - Wiring Devices: Requirements for electrical characteristics.

      - [___ hp.] [___] rated load amperes.

      - [___] volts, single or three phase, 60 Hz.

      - [___] amperes maximum fuse size, circuit breaker size and overcurrent protection.

      - [___] minimum circuit ampacity.

      - [___] percent minimum power factor at rated load.

    - Division 26 Electrical: Requirements for motors.

    - Disconnect Switch: Factory mount in control panel and on equipment.

- EXECUTION

  - EXAMINATION

    - Section 01 31 13 - Project Coordination: Coordination and project conditions.

    - Verify that roof curbs are installed and dimensions are as shown on shop drawings instructed by the manufacturer.

  - INSTALLATION

    - Provide materials in accordance with the specifications.

OR

    - Mount rooftop units on factory built roof-mounting curb providing watertight enclosure to protect ductwork and utility services. Install roof mounting curb level.

    - Locate remote panels where indicated [___].

    - Connect controls to remote locations.

    - Mount indoor units on vibration isolators.

    - Connect indoor units to supply and return ductwork with flexible connections.

    - Pipe refrigerant from indoor to outdoor unit

    - Pipe condensate from drain pan to nearest floor drain. Condensate drainage system [___].

  - MANUFACTURER'S FIELD SERVICES

    - Section 01 45 16.13 - Contractor’s Quality Control Program: Manufacturers’ field services.

    - Provide initial start-up and shutdown during first year of operation, including routine servicing and checkout.

  - DEMONSTRATION AND TRAINING

    - Demonstrate unit operation and maintenance.

  - SCHEDULES

Provide a schedule when more than one size or type unit is required.

The following examples may assist in developing such a schedule.

## UNITARY HEAT PUMP UNITS

| Drawing Code | RT-1 | RT-2 | RT-3 |
| --- | --- | --- | --- |
| Location |  |  |  |
| Manufacturer |  |  |  |
| Model |  |  |  |
| Supply Fan: | - | - | - |
| Air Flow |  |  |  |
| External Static Pressure |  |  |  |
| Fan Motor Power |  |  |  |
| Return, Exhaust Fan |  |  |  |
| Air Flow |  |  |  |
| External Static Pressure |  |  |  |
| Fan Motor Power |  |  |  |
| Cooling: | - | - | - |
| Sensible |  |  |  |
| Total |  |  |  |
| Evaporator entering DB temp |  |  |  |
| Evaporator entering WB temp |  |  |  |
| Evaporator leaving DB temp |  |  |  |
| Evaporator leaving WB temp |  |  |  |
| Condenser ambient air temp |  |  |  |
| Energy Efficiency Ratio |  |  |  |
| Heat |  |  |  |
| Input |  |  |  |
| Output |  |  |  |
| Outdoor DB Air Temp |  |  |  |
| Outdoor WB Air Temp |  |  |  |
| Co-efficient of Performance |  |  |  |
| Sound Rating Number |  |  |  |
| Compressor Power Input |  |  |  |
| Nominal Capacity |  |  |  |

## PACKAGED TERMINAL HEAT PUMP UNITS

| Drawing Code | AC-1 | AC-2 | AC-3 |
| --- | --- | --- | --- |
| Location |  |  |  |
| Manufacturer |  |  |  |
| Model Number |  |  |  |
| Total Cooling Capacity |  |  |  |
| Space supply: | - | - | - |
| Air Flow |  |  |  |
| Entering Air DB Temperature |  |  |  |
| Entering Air WB Temperature |  |  |  |
| Leaving Air DB Temperature |  |  |  |
| Leaving Air WB Temperature |  |  |  |
| Fan Motor |  |  |  |
| Heat Pump Source: | - | - | - |
| Water Flow |  |  |  |
| Water Temperature |  |  |  |
| Air Flow |  |  |  |
| Entering Air Temperature |  |  |  |
| Fan Pump Motor power |  |  |  |
| Heating |  |  |  |
| Heat Pump Capacity |  |  |  |
| Supplemental Coil Capacity |  |  |  |
| Number of stages |  |  |  |

## TERMINAL AIR CONDITIONING UNITS

| Drawing Code | TAC-1 | TAC-2 | TAC-3 |
| --- | --- | --- | --- |
| Location |  |  |  |
| Manufacturer |  |  |  |
| Model Number |  |  |  |
| Total Cooling Capacity |  |  |  |
| Cooling EER |  |  |  |
| Electric Resistance Heating Capacity |  |  |  |
| Reverse Cycle Heating Capacity |  |  |  |
| Reverse Cycle COP |  |  |  |

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2