READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Cable Trays” Work is shown in the Contract Documents. This section includes requirements for materials, equipment, tests for cable tray systems, including straight sections, bends, tees, elbows, dropouts, supports and accessories.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ASTM A 123 - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

    - NEMA FG 1 (National Electrical Manufacturers Association) - Fiberglass Cable Tray Systems

    - NEMA VE 1 (National Electrical Manufacturers Association) - Metallic Cable Tray Systems

    - NEMA VE 2 (National Electrical Manufacturers Association) - Metallic Cable Tray Installation Guidelines

    - NFPA 70 (National Fire Protection Association) - National Electrical Code

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: Include data indicating dimensions and finishes for each type of cable tray.

      - Manufacturer’s Installation Instructions: Include instructions for storage, handling, protection, examination, preparation, and installation.

      - Shop Drawings: Detail fabrication and installation of cable tray, including plans, elevations, and sections of components, and attachments to other construction elements. Designate components and accessories, including, but not limited to clamps, brackets, hanger rods, splice-plate connectors, expansion-joint assemblies, straight lengths, drop-offs, sweeps, and fittings.

      - Seismic Qualification Certificates: For cable trays, accessories, and components, from manufacturer. Move this to action submittals article

        - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

        - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

        - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

      - Design Calculations: Verify loading capacities for supports.

      - Coordination Drawings: Include floor plans and sections drawn to scale. Include scaled cable tray layout, support points, and relationships between components and adjacent structural and mechanical elements, vertical and horizontal offset and transitions, clearances for access above and to side of cable trays, and vertical elevation of cable trays above the floor or below bottom of ceiling structure.

      - Factory-certified test reports of specified products, complying with NEMA VE 1.

      - Field Test Reports: Provide grounding test locations and results.

      - Maintenance Data: For cable trays to include in the maintenance manuals specified in Division 1 General Requirements.

  - QUALITY ASSURANCE

    - Source Limitations: Obtain cable tray components through one source from a single manufacturer.

    - Listing and Labeling: Provide cable trays and accessories that are Listed and Labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to the Authority Having Jurisdiction, and marked for intended use for the location and environment in which they are installed.

    - Comply with NEMA VE 1, “Metal Cable Tray Systems,” for materials, sizes, and configurations.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

  - COORDINATION

    - Coordinate layout and installation of cable tray with other installations.

    - Revise locations and elevations from those indicated as required to suit field conditions and as approved by the Engineer.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Cooper B-Line

      - MP Husky

      - Legrand Cablofil.

      - Or Approved Equal.

  - MATERIALS AND FINISHES

    - Cable Trays, Fittings, and Accessories for Exterior Installations: Steel, complying with ASTM A570, Grade 33 for 14 gauge and heavier, and hot-dip galvanized after fabrication complying with ASTM A123.

    - Cable Trays, Fittings, and Accessories for Interior Installations: Aluminum, complying with Aluminum Association’s alloy 6063 for rails, rungs, and cable trays, and alloy 5052 for fabricated parts.

    - Protect steel hardware against corrosion by galvanizing according to ASTM B633 or cadmium plating according to ASTM B766.

    - Fabricate cable tray products with rounded edges and smooth surfaces.

    - Sizes and Configurations: Refer to Cable Tray Schedule on Drawings for specific requirements for types, materials, sizes, and configurations.

Select paragraph above or below.

    - Sizes and Configurations: Refer to Cable Tray Schedule for specific requirements for types, materials, sizes, and configurations.

  - CABLE TRAY SCHEDULE

Delete paragraph below if cable tray schedule is not shown on drawings.

    - Refer to Drawings.

Delete paragraphs below if cable tray schedule is shown on drawings. Modify cable tray schedule to suit Project.

    - Run Designation: [___]

Select tray type from the following three options below:

      - Ladder type:

        - Configuration: Two I-beam side rails with transverse rungs welded to side rails.

        - Rung Spacing: [6 inches for control cables,] [12 inches for power cables] on center.

        - Rung cable bearing surface: ¾ inch with radiused edges.

        - Radius-Fitting Rung Spacing: 9 inches at center of tray's width.

        - No portion of the rungs shall protrude below the bottom plane of side rails.

        - Structural Performance of Each Rung: Capable of supporting a 200-lb concentrated load, when tested according to NEMA VE 1.

      - Trough Type:

        - Configuration: Two longitudinal members (side rails) with a solid sheet over rungs exposed on the interior of the trough, or corrugated sheet with both edges welded to the side rails. Ventilated trough cable tray has rectangular holes punched along the width of the valleys of the corrugated bottom. Solid bottom is without holes.

        - Rung Spacing: Rungs or corrugations shall be spaced a maximum of 6 inches o.c. and have a minimum flat bearing surface of 2 inches.

        - Radius-Fitting Rung Spacing: 9 inches at center of tray's width.

        - Structural Performance: Capable of supporting a maximum cable load of 200-lb concentrated load, when tested according to NEMA VE 1.

          - Class Designation: Comply with NEMA VE 1, Class 12B OR Class 12C OR Class 20B OR Class 20C.

        - Splicing Assemblies: Bolted type using serrated flange locknuts.

        - Splicing Assembly Capacity: Splices located within support span shall not diminish rated loading capacity of cable tray.

        - Hardware and Fasteners: Steel, zinc plated according to ASTM B 633.

      - Channel Type: Channel with ventilated flat bottom with holes and slots to facilitate use of cable ties to secure cables.

      - Material and Finish: [Aluminum.] [Galvanized steel.]

      - Width: [6] [9] [12] [18] [24] inches.

      - Minimum Fitting Radius: [12] [24] inches.

Inside depth does not apply to channel type tray.

      - Inside Depth: [4] [5] [6] inches.

      - Structural Performance:  Capable of supporting a maximum cable load of 200lbs per rung or 800lbs per foot.

      - Length: 12 feet.

Select splice plates from 2 paragraphs below:

      - Splice Plates: Bolted type: high strength steel with 4 ribbed-neck carriage bolts with serrated flange locknuts.

      - Splice Plates: 6063-T6 aluminum with 4 square-neck bolts and serrated flange locknuts.

Covers are not allowed without prior approval of F & I

      - Cover: None

  - MATERIALS AND FINISHES

    - Steel:

      - Outdoor Installation: Steel  conforming to ASTM A1011, grade 33 for 14 gauge and heavier

      - Splice Plates: High strength steel splice plates with 4 ribbed neck carriage bolts with serrated flange locknuts each.

      - Finish: Hot-dip galvanized after fabrication, complying with ASTM A123.

        - Hardware: To match cable tray construction.

    - Aluminum:

      - Indoor Applications:  Alloy 6063- according to ANSI H35.1/H 35.1M for extruded components, and Alloy 5052 according to ANSI H35.1/H 35.1M for fabricated parts.

      - Splice Plates:

        - Bolted type, Aluminum alloy 6063-T6 with four square neck bolts and serrated flange locknuts each.

      - Hardware: Chromium-zinc-plated steel, ASTM F 1136.

    - Fabricate cable tray products with rounded edges and smooth surfaces.

  - CABLE TRAY ACCESSORIES

    - Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray.

Delete paragraph below if not used.

    - Barrier Strips: Same materials and finishes as cable tray.

    - Cable tray supports and connectors, including bonding jumpers, as required to install, support, and protect the cable tray system.

  - FIRESTOPPING

    - Flame-Safe compound capable of passing a one-hour or two-hour fire test per UL requirements.

    - Use Halon-free material that does not generate hydrogen gas while curing as manufactured by Thomas & Betts Corporation, 3M Corporation, Or Approved Equal.

  - WARNING SIGNS

    - 3/4” high, black letters on yellow laminated plastic nameplate, engraved with “WARNING!  DO NOT USE AS WALKWAY, LADDER, OR SUPPORT FOR LADDERS OR PERSONNEL – CABLES ADDED AFTER INITIAL INSTALLATION REQUIRE POS/F&I APPROVAL”.

  - SOURCE QUALITY CONTROL

    - Perform design and production tests according to NEMA VE 1.

- EXECUTION

  - EXAMINATION

    - Examine substrates for compliance with requirements for installation tolerances and other conditions affecting performance of cable trays. Do not proceed with installation until unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Install cable trays as a complete system, including fasteners, hold-down clips, support systems, barrier strips, adjustable horizontal and vertical splice plates, elbows, reducers, tees, crosses, cable dropouts, adapters, covers, and bonding.

    - Install cable trays so that the tray is accessible for cable installation and all splices are accessible for inspection and adjustment.

    - Join aluminum cable tray with splice plates; use four square-neck carriage bolts and locknuts.

    - Install cable tray level and plumb according to manufacturer’s written instructions, Coordination Drawings, original design, and referenced standards.

    - Remove burrs and sharp edges from cable trays.

    - Fasten cable tray supports securely to building structure as specified in Section 20 05 29 – Hangers and Supports and Section 26 05 48 - Seismic Controls for Electrical and Communication Work, unless otherwise indicated.

      - Locate and install supports according to NEMA VE 2.

Delete paragraph below if cable tray does not connect to equipment.

    - Make connections to equipment with flanged fittings fastened to cable tray and to equipment. Support cable tray independently of fittings. Do not carry weight of cable tray on equipment enclosure.

Delete paragraph below if expansion fittings are not required.

    - Install expansion connectors where cable tray crosses a building expansion joint and in cable tray runs that exceed 100 feet. Space connectors and set gaps according to NEMA VE 2.

    - Place supports so that spans do not exceed maximum spans on schedules and provide clearances shown on Drawings. Install intermediate supports when cable weight exceeds the load-carrying capacity of the tray rungs.

    - Construct supports from channel members, threaded rods, and other appurtenances furnished by cable tray manufacturer. Arrange supports in trapeze or wall-bracket form as required by application.

    - Support bus assembly to prevent twisting from eccentric loading.

    - Install center-hung supports for single-rail trays designed for 60 versus 40 percent eccentric loading condition, with a safety factor of 3.

    - Make cable tray connections and changes in direction or elevation using standard fittings.

    - Install only cables approved for use as tray cable in cable tray.

    - Locate cable tray above piping where practical.

    - Seal penetrations through fire and smoke barriers, including walls, partitions, floors and ceilings, after cables are installed, according to Section 07 84 00 - Firestopping.

If cable trays are sized for future cables, specify provisions for penetrations with sleeves through fire-rated partitions, or use “repairable” firestopping-penetration sealing material.

    - Sleeves for Future Cables: Install capped sleeves for future cables through firestopping-sealed cable tray penetrations of fire and smoke barriers.

    - Workspace: Install cable trays with sufficient space to permit access for installing cables.

Delete paragraph below if systems are not mixed.

    - Provide separate trays for cables of different systems, such as power, communications, and data processing; or of different insulation levels, such as 600V, 5kV, and 15kV.

    - Install barriers to separate cables of different voltage systems or to separate normal and emergency system cables.

    - When terminating a conduit to cable tray, use appropriate ground bushing to bond the conduit to the tray.

  - CONNECTIONS

    - Use anti-oxidant compound to prepare aluminum contact surfaces before assembly.

    - Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. Where manufacturer’s torque values are not indicated, use those specified in UL 486A and UL 486B.

    - Ground cable trays according to manufacturer’s instructions.

      - Provide #2 AWG minimum bare copper stranded cable, or larger as required by NFPA 70, for the entire length of cable tray and bond every section with F & I approved grounding clamps designed for cable trays. Connect ground conductor to building steel or ground grid.

      - Provide grounding bushing where conduit terminates at cable tray and bond conduit to tray.

      - When steel or aluminum tray are used as equipment grounding conductors, cable tray sections and fittings shall be marked to show minimum cross-sectional area in accordance with Article 318 of the NEC.

      - Connect ground conductor to building steel or ground grid.

  - CABLE INSTALLATION

    - Install cables only when each cable tray run has been completed and inspected.

    - Fasten cables on horizontal runs with cable clamps or cable ties according to NEMA VE 2. Tighten clamps only enough to secure the cable, without indenting the cable jacket. Install cable ties with a tool that includes an automatic pressure-limiting device.

    - Fasten cables on vertical runs to cable trays every 18 inches.

    - Fasten and support cables that pass from one cable tray to another or drop from cable trays to equipment enclosures. Fasten cables to the cable tray at the point of exit and support cables independent of the enclosure. The cable length between cable trays or between cable tray and enclosure shall be no more than 48 inches.

    - Tie MI cables down every 36 inches where required to provide a 2-hour fire rating and every 72 inches elsewhere. MI cable not allowed in Port standard, but if provided in OEM equipment.

    - In existing construction, remove inactive or dead cables from cable trays.

  - IDENTIFICATION

    - After installation of cable trays is completed, install warning signs as specified in Section 26 05 53 - Electrical Identification at 25-foot intervals in visible locations on cable trays, both sides of tray if both sides are visible.

  - FIELD QUALITY CONTROL

    - Grounding: Test cable trays to ensure electrical continuity of bonding and grounding connections. Maximum allowable resistance is 1 ohm.

    - Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

      - Visually inspect cable insulation for damage. Correct sharp corners, protuberances in cable trays, vibrations, and thermal expansion and contraction conditions, which may cause or have caused damage.

      - Verify that the number, size, and voltage of cables in cable trays do not exceed that permitted by NFPA 70. Verify that communications or data-processing circuits are installed separated cable trays from power circuits.

      - Verify that there are no intruding items such as pipes, hangers, or other equipment in the cable tray.

      - Remove dust deposits, industrial process materials, trash of any description, and any blockage of tray ventilation.

      - Visually inspect each cable tray joint and each ground connection for mechanical continuity. Check bolted connections between sections for corrosion. Clean and retorque in suspect areas.

      - Check for improperly sized or installed bonding jumpers.

      - Check for missing, incorrect, or damaged bolts, bolt heads, or nuts. When found, replace with specified hardware.

      - Perform visual and mechanical checks for adequacy of cable tray grounding; verify that all takeoff raceways are bonded to cable trays. Test entire cable tray system for continuity. Maximum allowable resistance is 1 ohm.

  - CLEANING

    - Upon completion of cable tray installation, including fittings, inspect exposed finish. Remove burrs, dirt, and construction debris and repair damaged finish, including chips, scratches, and abrasions.

  - PROTECTION

    - Protect installed cable trays and cables.

    - Install temporary protection for cables in open trays to safeguard exposed cables against falling objects or debris during construction. Temporary protection for cables and cable tray can be constructed of wood or metal materials and shall remain in place until the risk of damage is over

    - Repair damage to galvanized finishes with zinc-rich paint recommended by cable tray manufacturer.

    - Remove dirt and construction debris and repair damage to paint finishes including chips, scratches and abrasions with matching touchup coating recommended by cable tray manufacturer.

    - Provide final protection and maintain conditions, in a manner acceptable to manufacturer and Installer that ensure cable tray is without damage or deterioration at the time of Substantial Completion.

    - Repair damage to galvanized finishes with zinc-rich paint recommended by cable tray manufacturer.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions