READ THIS FIRST

The Engineer shall verify that the latest version of the Federal Aviation Administration Advisory Circular AC 150/5370-10, “Standards for Specifying Construction Of Airports” and that the latest version of the Federal Aviation Administration, Northwest Mountain Region Revision to AC 150/5370-10, “Standards for Specifying Construction Of Airports” are incorporated into this specification.

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Airport Underground Electrical Duct (FAA)” Work is shown in the Contract Documents.  Underground electrical duct and/or conduit for use with airport underground electrical and communication systems, shall be provided in accordance with the applicable provisions of FAA Item L-110, Airport Underground Electrical Duct Banks and Conduits, attached hereto.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

    - TBD

  - SUBMITTALS

    - Submit materials data in accordance with Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

- NOT USED

- NOT USED

- NOT USED

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

## Item L-110 Airport Underground Electrical Duct Banks and Conduits

## DESCRIPTION

110-1.1	This item shall consist of underground electrical ducts installed in accordance with this specification at the locations and in accordance with the dimensions, designs and details shown in the plans. This item shall include the installation of all underground electrical ducts or underground conduits. It shall also include all trenching, backfilling, removal and restoration of any paved areas; manholes, concrete encasement, mandreling installation of steel drag wires and duct markers, capping and the testing of the installation as a completed duct system ready for installation of cables, to the satisfaction of the Engineer.

## EQUIPMENT AND MATERIALS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

110-2.1	GENERAL. All equipment and materials covered by referenced specifications shall be subject to acceptance through manufacturer’s certification of compliance with the applicable specification when so requested by the Engineer.

110-2.2	STEEL CONDUIT. Galvanized rigid steel conduit complying to ANSI C80.1.  PVC-Coated rigid steel conduit complying to ANSI RN 1; coating thickness shall be 0.040 inch, minimum..

110-2.3	CONCRETE. Concrete shall conform to Item P-610, Structural Portland Cement Concrete using 1 inch (25 mm) maximum size coarse aggregate.

110-2.4	PLASTIC CONDUIT. 	Rigid plastic conduit, Schedule 40 and Schedule 80, complying to NEMA TC 2, UL 651A, rated for use with 90°C conductors under all installation conditions and labeled for underground use.

## CONSTRUCTION METHODS

110-3.1	GENERAL. The Contractor shall install underground ducts at the approximate locations indicated in the airport layout plans. The Engineer shall indicate specific locations as the work progresses. Ducts shall be of the size, material and type indicated in the plans or specifications. Where no size is indicated in the plans or specifications, the ducts shall be not less than 3 inches (75 mm) inside diameter. All duct lines shall be laid so as to grade toward handholes, manholes and duct ends for drainage. Grades shall be at least 3 inches (75 mm) per 100 feet (30 m). On runs where it is not practicable to maintain the grade all one way, the duct lines shall be graded from the center in both directions toward manholes, handholes, or duct ends. Pockets or traps where moisture may accumulate shall be avoided.

The Contractor shall mandrel each duct. An iron-shod mandrel, not more than 1/4 inch (6 mm) smaller than the bore of the duct shall be pushed through each duct by means of jointed conduit rods. The mandrel shall have a leather or rubber gasket slightly larger than the duct hole.

All ducts installed shall be provided with a No. 10 gauge galvanized iron or steel drag wire for pulling the permanent wiring. Sufficient length shall be left in manholes or handholes to bend the drag wire back to prevent it from slipping back into the duct. Where spare ducts are installed, as indicated on the plans, the open ends shall be plugged with removable tapered plugs, designed by the duct manufacturers, or with hardwood plugs conforming accurately to the shape of the duct and having the larger end of the plug at least 1/4 inch (6 mm) greater in diameter than the duct.

All ducts shall be securely fastened in place during construction and progress of the work and shall be plugged to prevent seepage of grout, water, or dirt. Any duct section having a defective joint shall not be installed.

All ducts, except steel conduit, installed under runways, taxiways, aprons and other paved areas shall be encased in a concrete envelope.

Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored.

Trenches for ducts may be excavated manually or with mechanical trenching equipment. Walls of trenches shall be essentially vertical so that a minimum of shoulder surface is disturbed. Blades of road patrols or graders shall not be used to excavate the trench. The Contractor shall ascertain the type of soil or rock to be excavated before bidding. All excavation shall be unclassified.

110-3.2	DUCTS ENCASED IN CONCRETE. Unless otherwise shown in the plans, concrete-encased ducts shall be installed so that the top of the concrete envelope is not less than 30 inches (45 cm) below the finished subgrade where installed under runways, taxiways, aprons, or other paved areas, and not less than 18 inches (45 cm) below finished grade where installed in unpaved areas. Ducts under paved areas shall extend at least 3 feet (90 cm) beyond the edges of the pavement or 3 feet (90 cm) beyond any underdrains which may be installed alongside the paved area. Trenches for concrete-encased ducts shall be opened the complete length before concrete is laid so that if any obstructions are encountered, proper provisions can be made to avoid them. All ducts for concrete encasements shall be placed on a layer of concrete not less than 3 inches (75 mm) thick prior to its initial set. Where two or more ducts are encased in concrete, the Contractor shall space them not less than 1-1/2 inches (37 mm) apart (measured from outside wall to outside wall) using spacers applicable to the type of duct. As the duct laying progresses, concrete not less than 3 inches (75 mm) thick shall be placed around the sides and top of the duct bank. End bells or couplings shall be installed flush with the concrete encasement where required.

When specified, the Contractor shall reinforce the bottom side and top of encasements with steel reinforcing mesh or fabric or other approved metal reinforcement. When directed, the Contractor shall supply additional supports where the ground is soft and boggy, where ducts cross under roadways, or where otherwise shown on the plans. Under such conditions, the complete duct structure shall be supported on reinforced concrete footings, piers, or piles located at approximately 5 foot (150 cm) intervals.

When clay or soapstone ducts are specified, they shall be installed with concrete encasement as described above. Clay conduit shall be of the single-bore type. Where the self-centering socket-joint type of single clay duct is used, conduit shall be built up, tier by tier and separated only by sufficient mortar or fine aggregate concrete to bed the ducts evenly and fill all voids between ducts. Single ducts shall be jointed together and the joints grouted with Portland cement mortar. A suitable gasket (of rubber or other approved material) shall first be placed in the receptacle end of the duct, prior to the joining operation, in order to exclude all mortar from the duct.

Where the square bore butt-joint type of clay duct, single or multi-cell, is used, sections shall be aligned with at least four steel dowel pins and joints wrapped with duct tape 6 inches (150 mm) wide and lapped 6 inches (150 mm). All joints in a bank of single-bore ducts shall be staggered, beginning evenly from the manhole or handhole, by means of short lengths 6, 8, 9, 12 and 15 inches (150, 200, 230, 300, 380 mm) long. Cement mortar shall be trowled around each and every joint. Voids in the duct bank, caused by the external shape of the corners of the conduit, shall also be filled with mortar. The joining and joints of soapstone duct shall be done in accordance with the manufacturer's recommendations.

110-3.3	DUCTS WITHOUT CONCRETE ENCASEMENT. Trenches for single-duct lines shall be not less than 6 inches (150 mm) nor more than 12 inches (300 mm) wide and the trench for 2 or more ducts installed at the same level shall be proportionately wider. Trench bottoms for ducts without concrete encasement shall be made to conform accurately to grade so as to provide uniform support for the duct along its entire length.

A layer of fine earth material, at least 4 inches (100 mm) thick (loose measurement) shall be placed in the bottom of the trench as bedding for the duct. The bedding material shall consist of soft dirt, sand or other fine fill and it shall contain no particles that would be retained on a 1/4 inch (6 mm) sieve. The bedding material shall be tamped until firm.

Unless otherwise shown in plans, ducts for direct burial shall be installed so that the tops of all ducts are at least 30 inches (45 cm) below the finished grade.

When two or more ducts are installed in the same trench without concrete encasement, they shall be spaced not less than 2 inches (50 mm) apart (measured from outside wall to outside wall) in a horizontal direction and not less than 6 inches (150 mm) apart in a vertical direction.

Trenches shall be opened the complete length before duct is installed so that if any obstructions are encountered, proper provisions can be made to avoid them.

110-3.4	DUCT MARKERS. The location of the ends of all ducts shall be marked by a concrete slab marker 2 feet (60 cm) square and 4 inches (100 mm) thick extending approximately 1 inch (25 mm) above the surface. The markers shall be located above the ends of all ducts or duct banks, except where ducts terminate in a handhole, manhole, or building.

The Contractor shall impress the word “duct” on each marker slab. He shall also impress on the slab the number and size of ducts beneath the marker. The letters shall be 4 inches (100 mm) high and 3 inches (75 mm) wide with width of stroke 1/2 inch (12 mm) and 1/4 inch (6 mm) deep or as large as the available space permits.

110-3.5	BACKFILLING. After concrete-encased ducts have been properly installed and the concrete has had time to set, the trench shall be backfilled in at least two layers with excavated material not larger than 4 inches (100 mm) in diameter and thoroughly tamped and compacted to at least the density of the surrounding undisturbed soil. If necessary to obtain the desired compaction, the backfill material shall be moistened or aerated as required.

Trenches shall not be excessively wet and shall not contain pools of water during backfilling operations.

The trench shall be completely backfilled and tamped level with the adjacent surface: except that, when sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement.

Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

For ducts without concrete envelope, 8 inches (200 cm) of sand, soft earth, or other fine fill (loose measurement) shall be placed around the ducts and carefully tamped around and over them with hand tampers. The remaining trench may be filled with regular run of excavated material and thoroughly tamped as specified above.

110-3.6	RESTORATION. Where sod has been removed, it shall be replaced as soon as possible after the backfilling is completed. All areas disturbed by the trenching, storing of dirt, cable laying, pad construction and other work shall be restored to its original condition. The restoration shall include any necessary topsoiling, fertilizing, liming, seeding, sprigging, or mulching. All such work shall be performed in accordance with the FAA Standard Turfing Specifications. The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.

## METHOD OF MEASUREMENT

110-4.1	Underground duct shall be measured by the linear feet (meter) of duct installed, measured in place, completed and accepted. Separate measurement shall be made for the various types and sizes.

## BASIS OF PAYMENT

110-5.1	Payment will be made at the contract unit price for each type and size of single-way or multi-way duct completed and accepted. This price shall be full compensation for furnishing all materials and for all preparation, assembly and installation of these materials and for all labor, equipment, tools and incidentals necessary to complete this item.

A.	Payment will be made under:

1.	Item L-110-5.1 - Single-Way or Multi-Way Electrical Duct--per linear foot (meter)

## MATERIAL REQUIREMENTS

- FAA Standard Turfing Specifications,

- Fed.Spec.W-C-571, Conduit and Fittings, Non-metal, Rigid; (Asbestos-Cement or Fire-Clay Cement), (For Electrical Purposes),

- Fed.Spec.W-C-1094, Conduit and Fittings; Non-metallic, Rigid, (Plastic),

- FAA Item L-110, Installation of Airport Underground Electrical Duct,

- Item P-610,

- Underwriters Rigid Metal Conduit Laboratories Standard 6,

- Underwriters Fittings for Conduit and Outlet Boxes Laboratories Standard 514,

- Underwriters Impregnated-Fiber Electrical Conduit Laboratories Standard 543,

- Underwriters Intermediate Metal Conduit Laboratories Standard 1242,

End of Item