READ THIS FIRST

Notice to the Design Engineer; please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Underground Ducts and Manholes” Work is shown in the Contract Documents. This section includes the requirements for trenching, backfilling and installation of underground conduits, ducts and ductbanks, and the design, fabrication, delivery and installation of pull boxes, handholes and manholes.

    - Definitions

      - Duct: Electrical conduit and other raceway, either metallic or nonmetallic, used underground, embedded in earth or concrete.

      - Ductbank: 2 or more conduits or other raceway installed underground in the same trench or concrete envelope.

      - Handhole: An underground junction box in a duct or duct bank.

      - Manhole: An underground utility structure, large enough for a person to enter, with facilities for installing and maintaining cables.

      - Vault: An underground utility structure, large enough for a person to enter, with facilities for installing, operating, and maintaining equipment and wiring.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ASTM (American Society for Testing and Materials)

    - NFPA 70 (National Fire Protection Association) - National Electrical Code

    - WSDOT/APWA Specifications, Section 6-02.3

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product data for accessories for manholes and handholes, conduit and duct, duct bank materials, and miscellaneous components.

      - Shop drawings showing details and design calculations for precast manholes and handholes, including reinforcing steel. Stamp drawings with seal of Professional Structural Engineer licensed in the State of Washington.

      - Duct-Bank Coordination Drawings: Show duct profiles and coordination with other utilities and underground structures. Include plans and sections, drawn to scale and show bends and locations of expansion fittings. Drawing shall be signed and sealed by a qualified Professional Engineer licensed in the State of Washington.

      - Certificate for concrete and steel used in underground precast concrete utility structures, according to ASTM C 858.

      - Qualification Data: For Professional Engineer and testing agency responsible for testing nonconcrete handholes and boxes

      - Inspection report for factory inspections, according to ASTM C 1037.

      - Record Documents: Show dimensioned locations of underground ducts, handholes, and manholes from nearest building or permanent structure.

  - QUALITY ASSURANCE

    - Listing and Labeling: Provide products that are Listed and Labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to the Authority Having Jurisdiction, and marked for intended use for the location and environment in which they are installed.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

    - Comply with ANSI C2 “National Electrical Safety Code” for components and installation.

  - COORDINATION

    - Coordinate layout and installation of ducts, manholes, and handholes with final arrangement of other utilities as determined by field verification. Revise locations and elevations from those indicated as required to suit field conditions and ensure that duct runs drain to manholes and handholes. Contractor shall coordinate all modifications with the Engineer prior to final installation.

  - SAFETY REQUIREMENTS

    - Comply with safety and protection requirements of Section 26 00 00 - Electrical Work - General.

    - Perform Work in accordance with the safety requirements of the Department of Labor Occupational Safety and Health Administration, Volume 36, Number 75, Part II, Subpart P, “Excavations, Trenching, and Shoring,” and with Section 7 of the Manual of Accident Prevention in Construction as published by the Association General Contractors of America, Inc.

    - Educate supervisors and employees on safety requirements and practices to be followed during the course of the Work.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver ducts to site with ends capped. Store nonmetallic ducts with supports to prevent bending, warping, and deforming.

    - Store precast concrete units at site as recommended by manufacturer to prevent physical damage. Arrange so identification markings are visible.

    - Lift and support precast concrete units only at designated lifting or supporting points.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manholes, Handholes and Vaults: Subject to compliance with requirements, provide products by one of the following:

      - Utility Vault / Oldcastle Precast Company.

      - Shaw PIPE; Division of Shawcor Co.

      - American Concrete.

      - Or Approved Equal.

  - CONDUIT AND DUCTS

    - Metallic Conduit:

      - Galvanized Rigid Steel Conduit (GRC): ANSI C80.1

      - PVC-Coated Rigid Steel Conduit: ANSI RN 1. Coating thickness shall be 0.040 inch, minimum.

    - Nonmetallic conduit: Use underground only for medium-voltage and low-voltage applications

      - Rigid Plastic Conduit: NEMA TC 2, UL 651A, Schedule 40 and Schedule 80 PVC, rated for use with 90°C conductors under all installation conditions and labeled for underground use.

Select sub-paragraph above or below. HDPE may be used for marine applications only.

      - Rigid Plastic Underground Conduit: High-density polyethylene, Schedule 40 and Schedule 80.

      - LFNC: UL 1660.

  - CONDUIT FITTINGS

    - Steel Fittings: Zinc-coated, cast malleable, ferrous metal, threaded fittings, with neoprene cover gasket on each fitting installed outdoors.

    - PVC Conduit and Tubing Fittings: NEMA TC 3. Provide PVC fittings for PVC conduit and suitable watertight connections where PVC conduit connects to galvanized steel conduit.

    - “Mogul Fittings”: Provide “Mogul” size fittings for all conduit.

    - Seal Bushings: O.Z. compound bushing on each conduit entering a building from outside underground and on each conduit passing from one space into another, which is normally at a lower temperature.

    - Hubs: Appleton “Hub” or “Hub-U” series, Thomas & Betts “370” series, Or Approved Equal hub on each conduit terminating in a box where a hub was not previously provided.

    - Unions: Appleton Type “EC”, Thomas & Betts “Erickson Coupling” conduit unions, Or Approved Equal where necessary.

  - DUCT SUPPORTS/SPACERS

    - Rigid PVC spacers selected to provide 3 1/2” minimum duct spacings and concrete cover depths indicated, while supporting ducts during concrete pour. Refer to drawing details for additional duct spacing requirements.

  - PULL BOXES

    - Cast Metal Boxes: Cast aluminum, sized as indicated on Drawings, with outside flanges and recessed, gasketed cover for flush mounting. Non-skid finish on cover with legend reading “ELECTRIC” or “SIGNAL” as appropriate.

  - HANDHOLES

    - General: Precast concrete or structural plastic, as indicated on Drawings. Walls and bottom shall be constructed to support rating of cover. Frame and cover shall form top of enclosure, with the following standard features:

      - Cover with insert or other device to facilitate lifting.

      - Cover with locking devices similar to REA, FARGO, Or Approved Equal.

      - Drain hole in base, 2-inch minimum diameter.

      - Knockouts in sides of adequate number and spacing to accommodate ductbank shown.

    - Street Lighting: Reinforced plastic mortar designed and tested to temperatures of - 50°F meeting ASTM D635-91 flammability test.

Modify paragraph below as required for Project.

    - Handhole Covers: Reinforced concrete or cast iron, capable of supporting designed loads. Where located in roadways or aprons, covers shall be designed to support H20 or H40, minimum loading. Cast iron cover with cast-in legend “ELECTRIC” or “SIGNAL” as appropriate. Machine cover-to-frame bearing surfaces. Precast concrete strength to support H40 covers. Cover hinges concealed, with hold-open ratchet assembly.

  - PRE-CAST MANHOLES AND VAULTS (AASHTO RATED)

    - Precast Concrete Units: Interlocking, mating sections complete with accessory items, hardware, and features as indicated on Drawings. Include concrete knockout panels 1-1/2 to 2 inches thick for future conduit entrances and sleeves for ground rods.

    - Duct Entrances in Manhole Walls: Cast end-bell or duct-terminating fitting in wall for each entering duct.

      - Type and size shall match fittings to duct or conduit to be terminated.

      - Fittings shall align with elevations of approaching ducts and be located near interior corners of manholes to facilitate racking of cable.

    - Ground Rod Sleeve: Provide a 3-inch PVC conduit sleeves in manhole floors 2 inches from the wall adjacent to, but not underneath, the duct routed from the facility.

    - Design structure according to ASTM C 858.

    - Joint Sealant: Continuous extrusion of asphaltic butyl material with adhesion, cohesion, flexibility, and durability properties necessary to withstand the maximum hydrostatic pressures at the installation location with the ground water level at grade.

    - Source Quality Control: Inspect structures according to ASTM C 1037. Units shall be capable of supporting specified loads.

  - CAST-IN-PLACE MANHOLES AND VAULTS

    - Description: Underground utility structures, constructed in place, complete with accessories, hardware, and features. Include concrete knockout panels for conduit entrance and sleeve for ground rod.

    - Manhole covers shall be reinforced concrete or cast iron and capable of supporting loads that are expected for the installed location. Where located in roadways H20 or aprons H40, covers to support minimum loading. Designer shall evaluate other applications during design.

    - Where manholes have drain holes in bottom, provide at least two feet of gravel under manhole.

    - Provide 4” drain line from manholes to sump or storm sewer.

If possible, install manholes and vaults that are one size larger than that required by the NEC.

    - Walls and Floors: Reinforced concrete to strength of covers.  Provide at least two holes for drainage, two-inch minimum diameter, except where Drawings show an internal sump with sump pump.

    - Manhole Covers: Reinforced concrete or cast iron, capable of supporting designed loads. Where located in roadways or aprons, covers shall be designed to support H20 minimum loading. Cast iron cover with cast-in legend “ELECTRIC” or “SIGNAL” as appropriate. Machine cover-to-frame bearing surfaces.

  - ACCESSORIES

    - Frames, Covers and Ring Components:   Comply with structural design loading specified for manhole.

      - Frame and Cover: Weatherproof, reinforced concrete or cast-iron and capable of supporting loads that are expected for the installed location.

        - Cover H20 highway rated in roadways or H40 highway rated in aprons. Designer shall evaluate other applications during design.

        - Cover Finish: Nonskid finish shall have a minimum coefficient of friction of 0.50.

        - Special Covers: Recess in face of cover designed to accept finish material in paved areas.

      - Cover Legend: Manhole ID welded into cover, cast iron with cast-in legend. Manhole Ring Components: Precast concrete rings with dimensions and strength matched to those of highway rated roof opening.

        - Mortar for Ring and Frame and Cover Joints: Strength to match highway rated cover.

        - Where required, seal joints watertight using preformed plastic or rubber conforming to ASTM C 990. Install sealing material according to the sealant manufacturers' printed instructions.

    - Sump Piping: Provide sump pipe and sump in high water table areas where low-voltage power can be made readily available.

    - Duct Supports: Rigid PVC spacers selected to provide 3 1/2” minimum duct spacings and concrete cover depths indicated, while supporting ducts during concrete pour.

    - Manhole and Vault Lifting Means

      - Pulling Eyes in Walls: Eyebolt with reinforcing bar fastening insert. 2-inch diameter eye, 1-inch by 4-inch bolt. Working load with 6 inch embedment in 4000 psi concrete: 13,000 pounds minimum tension.

      - Pulling and Lifting Irons in Floor: 7/8-inch-diameter, hot-dipped galvanized, bent steel rod, stress relieved after forming, and fastened to reinforced rod. Exposed triangular opening. Ultimate yield strength: 40,000 pounds shear and 60,000 pounds tension.

Delete paragraph E and others below where not required. Manufacturer’s standard precast units have a sump consisting of a depression in the floor only, with no frame or grate.

    - Sump Frame and Grate (Cast-in-place units only):  ASTM A 48/A 48M, Class 30B, gray cast iron. Comply with FS RR-F-621, Type VII for frame and Type I for cover

    - Bolting Inserts for Cable Stanchions: Threaded precast channel inserts of hot-dipped galvanized or stainless steel; 3’-0” on center; 1/2-inch internal diameter by 2-3/4 inches deep, flared to 1-1/4 inch minimum at base. Tested ultimate pull-out strength: 12,000 pounds minimum.

    - Expansion Anchors for Installation After Concrete is Cast: Zinc-plated carbon steel wedge type with stainless-steel expander clip, 1/2-inch bolt size, 5300-pound rated pull-out strength, and 6800-pound rated shear strength minimum. Cast in-place inserts not allowed unless cast by vault manufacturer.

    - Cable Rack Assemblies – heavy duty non-metallic 50% glass reinforced nylon or other non-metallic material having equal mechanical strength, thermal resistance, chemical resistance, dielectric strength and physical properties

      - Cable Stanchions: Nominal 36 inches high by 4 inches wide, with multiple arm mounting holes and recessed bolt mounting holes.

      - Cable Arms: Arranged for secure drop in attachment in horizontal position at any location on cable stanchion, and capable of being locked in position. Arms shall be available in lengths ranging from 3 inches with 450 lb. minimum capacity to 20 inches with 250 lb. minimum capacity. Top of arm shall be nominally 4 inches wide and shall have slots along full length for cable ties.

    - Cable Support Insulators: High glaze, wet-process porcelain arranged for mounting on cable arms.

    - Ground Rods: Ensure rods are copper bonded 5/8-inch by 10-foot minimum.

    - Ground Rod Sleeves: 3 inch PVC conduit sleeve in manhole floors 2 inches from the wall adjacent to, but not underneath, the ducts routed from the facility.

    - Ground Wire: Stranded bare copper, #2 AWG minimum. #4, AWG

Engineer to add additional approved manufacturer/product number for Duct Sealing Compound. A minimum of two items is required otherwise a competition waiver is required.

    - Duct Sealing Compound: 3M Fireseal, [        ], Or Approved Equal. Non-hardening, safe for human skin contact, not deleterious to cable insulation, workable at temperatures as low as 35°F withstands temperature of 300°F without slump, and adheres to clean surfaces of plastic ducts, metallic conduits, conduit coatings, concrete, masonry, lead, cable sheaths, cable jackets, insulation materials, and the common metals.

Delete paragraph below if portable ladder is not required for Project.

    - Ladder: UL-listed, heavy-duty fiberglass material, specifically designed for electrical manhole use. Minimum length equal to the distance from the deepest manhole floor to grade plus 3 feet., fiberglass material,

  - DUCTBANK CONCRETE

    - Material: Provide in accordance with Section 03 30 00 - Cast-in-Place Concrete and as follows:

      - Gravel: 3/8” maximum.

      - Slump: 4” maximum.

      - Compressive strength: 3,000 psi at 28 days.

      - Color: Dye ductbank concrete red.

      - Reinforcing (except when GRC is used): Steel conforming to ASTM A15. Provide #4 rebar top and bottom, 2’-0” lap at splices (typical 4 places) and #4 @ 18” on center around perimeter with 3” minimum cover.

  - BACKFILL MATERIAL

    - Designer shall coordinate trenching and backfill with Civil trenching and backfill sections.

      - Lower Trench Portion (surrounding ductbank): Sandy silt, clay silt, sand clay or other material free of stones and conglomerates larger than 2”

      - Upper Trench Portion (one foot above ductbank up to grade): On-site backfill material consisting of rock, soil or soil-rock mixture containing no rocks or lumps over 6”

Coordinate trenching and backfill with Division 33 Utilities sections.

    - Reinforced Concrete Ductbanks:

      - Below Concrete Encasement: 6” minimum compacted 5/8” minus crushed rock.

      - Above Concrete Encasement: 3” minimum sand.

      - Upper Trench:

        - Areas Under Pavement: Controlled Density Fill.

          - Content: A mixture of Portland cement, fly ash, aggregates, water and admixtures proportioned to provide a non-segregating, self-consolidating and free flowing material which will result in a hardened, dense, non-settling and excavatable fill. Batch and mix in accordance with Section 6-02.3 of the WSDOT/APWA Specifications to provide a flowing, non-segregating mix with a slump between 6” and 8”.

        - Areas Not Under Pavement: Select Native Fill.

          - Unsaturated excavated earth free of rocks, broken concrete and debris 6” and larger, and compacted in 12” lifts to prevent settlement.

    - Direct-Burial Conduit

      - Initial Bedding: 3” of sand below conduits.

      - Secondary Bedding: Unsaturated excavated earth free of rocks, broken concrete and debris 2” and larger, and compacted to 6” minimum above conduits.

      - Upper Trench:

        - Areas Under Pavement: Controlled Density Fill.

          - Content: A mixture of Portland cement, fly ash, aggregates, water and admixtures proportioned to provide a non-segregating, self-consolidating and free flowing material which will result in a hardened, dense, non-settling and excavatable fill. Batch and mix in accordance with Section 6-02.3 of the WSDOT/APWA Specifications to provide a flowing, non-segregating mix with a slump between 6” and 8”.

        - Areas Not Under Pavement: Select Native Fill.

          - Unsaturated excavated earth free of rocks, broken concrete and debris 6” and larger, and compacted in 12” lifts to prevent settlement.

  - CONTROLLED DENSITY FILL (CDF)

    - CDF shall be a mixture of Portland cement, fly ash, aggregates, water and admixtures proportioned to provide a non-segregating, self-consolidating and free flowing material which will result in a hardened, dense, non-settling and excavatable fill.

    - CDF shall be used as fill above utilities wherever non-settling backfill is required.

    - CDF shall be batched and mixed in accordance with Section 6-02.3 of the WSDOT/APWA Specifications.

    - CDF shall be batched to provide a flowing, non-segregating mix with a slump between 6” and 8”.

- EXECUTION

  - EXAMINATION

    - Examine site to receive ducts and manholes for compliance with installation tolerances and other conditions affecting performance of the underground ducts and manholes. Do not proceed with installation until unsatisfactory conditions have been corrected.

    - Existing Utilities: Locate all existing utilities in the area prior to performing any excavation.

  - EARTHWORK

    - Comply with Section 31 00 00 - Earthwork.

    - Trenching:

      - Comply with OSHA/WISHA safety standards for trenching, including stable slope and shoring requirements.

      - Depth: Refer to Drawings for trench depth requirements. Correct points of over-excavation using mechanically-compacted backfill to form a smooth trench bottom.  18 inch minimum cover over top of conduit ductbank.

      - Width: Excavate to minimum width consistent with stability of sides.

      - Slope: Slope trenches so that conduit and ducts drain toward manholes and handholes and away from buildings and equipment.

      - Rock Excavation: Where rock pad is used for conduit trench, overexcavate 6” below the ductbanks and refill and compact with selected backfill material of same composition.

      - Muck Excavation: Where muck or unstable material is encountered, over-excavate and backfill to attain proper grade with coarse sand, gravel, or Controlled Density Fill.

      - Stockpile backfill material in an orderly manner; a sufficient distance from the trench to avoid overloading trench banks.

      - Bedding: The entire bottom of the excavation is to be firm, stable, and at uniform density.

    - Excavating for Handholes, Manholes and Vaults: Provide 12” minimum clearance between outer surfaces of unit and embankment or timber used for shoring.

  - RACEWAY APPLICATIONS

    - Refer to Specifications and Drawings for raceway materials. Where not specified otherwise, use metallic conduit above and underground.

    - Metallic Conduit: Only use as specified in Section 26 05 33 - Raceways and Boxes.

    - Nonmetallic conduit: Use underground only.

      - Underground in Reinforced, Concrete-Encased Ductbanks: For medium-voltage and low-voltage applications. Use Schedule 40 Rigid Plastic Conduit as standard. Use rigid steel conduit on turns 45° or greater. Use Schedule 80 Rigid Plastic Conduit under roadways and in runway areas.

      - Underground Direct-Burial: For low-voltage applications only. Provide rigid plastic conduit, NEMA TC 2, Schedule 40 PVC (except rigid steel under roadways and either rigid steel or Schedule 80 in runway areas), with NEMA TC3 PVC conduit and tubing fittings.

    - All underground conduit shall be a minimum of two-inch standard trade size, except it is permissible to use one-inch conduit to lighting poles.

    - Use PVC fittings for PVC conduit and suitable water-tight connections where PVC conduit connects to galvanized steel conduit.

  - CONDUIT AND DUCT INSTALLATION

    - Install conduit and ducts as indicated on Drawings and according to manufacturer’s written instructions.

    - Slope: For ductbanks and conduits without profiles, pitch ducts minimum of 4 inches per 100 feet to drain toward manholes and handholes and away from buildings and equipment. Slope ducts from a high point in runs between 2 manholes to drain in both directions. For ductbanks with profiles, install the ductbank at the elevation as shown on the drawings.

    - Curves and Bends: Use manufactured galvanized rigid steel elbows for stub-ups at equipment and at building entrances with a minimum radius of 36 inches. Use manufactured long sweep bends with a minimum radius of 25 feet both horizontally and vertically at other locations. Do not exceed 20 degrees for field bends.

    - Make joints in ducts and fittings watertight according to manufacturer’s instructions. Stagger couplings so those of adjacent ducts do not lie in the same plane.

    - Duct Entrances to Manholes and Handholes: Space end bells approximately 10 inches on center for 5-inch ducts and varied proportionately for other duct sizes. Change from regular spacing to end-bell spacing 10 feet from the end bell without reducing duct line slope and without forming a trap in the line. Grout end bells into manhole walls from both sides to provide watertight entrances. Core drill entrances where knockouts do not exist.

    - Building Entrances: Transition from underground duct to rigid steel conduit 5 feet minimum outside the building wall. Use fittings manufactured for the purpose. Follow appropriate installation instructions below:

      - Concrete-Encased Ducts: Install reinforcing in ductbanks passing through disturbed earth near buildings and other excavations. Provide ductbank support at wall without reducing structural or watertight integrity of building wall.

      - Direct-Buried, Non-encased Duct Entering Non-waterproofed Walls: Provide a Schedule 40 galvanized-steel pipe sleeve for each duct. Caulk space between the conduit and sleeve with duct-sealing compound on both sides for moisture-tight seal.

      - Waterproofed Wall and Floor Entrances: Provide a watertight entrance-sealing device with the sealing gland assembly on the inside. Anchor device into masonry construction with one or more integral flanges. Secure membrane waterproofing to the device to make permanently watertight.

    - Separation Between Direct-Buried, Non-Encased Ducts: Provide 3 inches minimum separation for like services, and 12 inches minimum between power and signal ducts.

    - Concrete-Encased Nonmetallic Ducts: Support on plastic separators coordinated with duct size and required duct spacing, and install according to the following:

      - Separator Installation: Space separators close enough to prevent sagging and deforming of ducts or at 8 feet maximum, and secure separators to the earth and to ducts to prevent floating during concreting. Do not use tie wires or reinforcing steel that may form conductive or magnetic loops around ducts or duct groups.

      - Concrete: Do not pour concrete until conduit installation has been approved. Spade concrete carefully during pours to prevent voids under and between conduits and at the exterior surface of the envelope. Do not use power-driven agitating equipment unless specifically designed for duct bank application. Pour each ductbank between manholes or other terminations in one continuous operation. When more than one pour is necessary, terminate each pour in a vertical plane and install 3/4-inch reinforcing rod dowels extending 18 inches into the concrete on both sides of the joint near the corners of the envelope.

      - Reinforcing: Reinforce ductbanks where they cross disturbed earth and where indicated on Drawings.

      - Forms: Use the walls of the trench to form the side walls of the duct bank where the soil is self-supporting and the concrete envelope can be poured without soil inclusions; otherwise, use forms.

      - Minimum Clearances Between Ducts: 3 inches between ducts and exterior envelope wall, 3 inches between ducts for like services, and 12 inches between power and signal ducts.

      - Depth: Except as otherwise indicated, install top of duct bank at least 18 inches below finished grade in non-traffic areas and at least 24 inches below finished grade in vehicular traffic areas.

    - Stub-Ups: Use rigid steel conduit for stub-ups through concrete to equipment. Install insulated grounding bushings at the conduit terminations. For equipment mounted on outdoor concrete pads, extend steel conduit a minimum of 2 feet beyond the edge of the pad. Couple steel conduits to the ducts with adapters designed for the purpose and then encase the coupling with 3 inches of concrete.

    - Sealing: Provide temporary closure at all duct terminations in manholes and vaults installed in this Project. Use sealing compound and plugs to withstand a minimum of 15 psi hydrostatic pressure.

    - Pulling Cord: Install 100-pound- test nylon cord in installed ducts, including spares.

    - Warning Tape: Bury warning tape approximately 12 inches above all concrete-encased ducts and duct banks. Align tape parallel to and within 3 inches of centerline of duct bank. Provide an additional warning tape for each 12-inch increment of ductbank width over a nominal 18 inches. Space additional tapes 12 inches apart, horizontally.

  - BACKFILLING

    - Backfill only after all necessary inspections and tests have been performed.

    - Remove all debris, rocks, broken concrete, and formwork before backfilling trenches.

    - Use Controlled Density Fill under pavement areas or wherever non-settling backfill is required.

    - Deposit backfill in layers with materials described in Article 2.11, “Backfill Material.” Uniformly spread and compact backfill with suitable power tampers to the density of the adjacent soil and in such a manner so as not to disturb the alignment of the conduit. If settlement occurs, refill, compact and smooth off to conform to the surface of the ground.

    - Restore surface features at areas disturbed by excavation, and reestablish original grades.

      - Replace removed sod as soon as possible after backfilling is completed.

      - Restore all areas disturbed by trenching, storing of dirt, cable laying, and other Work.

      - Restore vegetation and provide necessary topsoil, fertilizer, lime, seed, sod, sprigging, or mulching.

      - Replace disturbed paving.

  - VAULT, MANHOLE AND HANDHOLE INSTALLATION

    - Install as indicated on Drawings according to manufacturer’s written instructions and ASTM C 891.

      - In areas which are subjected to vehicular traffic, install units plumb and level and with orientation and depth coordinated with arrangement of connecting ducts to minimize bends and deflections required for proper entrances.

      - In areas which are not subject to vehicular traffic, install so that manhole lid is 2” above surrounding dirt or gravel, and with orientation and depth coordinated with arrangement of connecting ducts to minimize bends and deflections required for proper entrances

      - Support units on a level bed of crushed stone or gravel, graded from the 1/2-inch sieve to the No. 4 sieve and compacted to the same density as the adjacent undisturbed earth.

      - Drainage: Where manholes have drain holes in the bottom, provide two feet minimum of gravel below the drain hole or provide a drain line to the nearest storm drain.

    - Grounding:

      - Ground underground ducts and utility structures according to Section 26 05 26 - Grounding.

      - Handhole and Small Manholes: Install two ground rods through floor in each medium voltage handhole and small manhole with top protruding 4’ above floor

      - Large Manholes and Vaults: Install four ground rods through floor in each medium voltage manhole with top protruding 4” above floor. Refer to Section 26 05 26 Grounding.

      - Ensure rods are copper 5/8 inch by 10 foot minimum.

      - Provide #4/0 ground wire in ductbank. Provide #4/0 bare copper ground wire in manhole, attached to wall, attached at 24 inches on center and mounted minimum 6 inches above floor.

      - Provide #2 stranded copper equipment ground minimum in each raceway in use.

    - Hardware: Install removable hardware, including pulling eyes, cable stanchions, cable arms, and insulators, as required for installation and support of cable and conductors and as indicated on Drawings.  Select arm lengths to be long enough to provide spare space for future cables, but short enough to preserve adequate working clearances in enclosure.

      - Field-Installed Bolting Anchors: Do not drill deeper than 3-7/8 inches for field-installed anchor bolts. Use a minimum of 2 anchors for each cable stanchion.

    - Train cables neatly around corners and secure to walls or ceiling using cable clamps with expansion anchors.

    - Field cut openings for ducts and conduits according to enclosure manufacturer's written instructions. Cut wall of enclosure with a tool designed for material to be cut. Size holes for terminating fittings to be used, and seal around penetrations after fittings are installed.

    - For enclosures installed in asphalt paving and subject to occasional, nondeliberate, heavy-vehicle loading, form and pour a concrete ring, encircling and in contact with enclosure, and with top surface secured to top of box cover frame. Bottom of ring shall rest on controlled density fill per Engineer of record.

      - Concrete: 3000 psi, 28-day strength with a troweled finish.

      - Dimensions: Minimum 10 inches wide by 12 inches deep or per Engineer of record.

  - SUMP PIPING

    - Provide sump pipe and sump in high water table areas where low voltage power can be made readily available.

  - GROUNDING

    - Ground underground ducts and utility structures according to Section 26 05 26 Grounding.

  - IDENTIFICATION

    - Identify raceways, cables and equipment as specified in Section 26 05 53 - Electrical Identification.

    - Label raceways entering concealed locations from exposed locations as to the destination via the concealed area.

  - TESTING AND CLEANING

    - Pull brush through full length of ducts. Use round bristle brush with a diameter 1/2-inch greater than internal diameter of duct. Clean internal surfaces of vaults, manholes and handholes, including sump.

    - Duct Integrity: Swab out ducts with a mandrel 1/4 inch smaller in diameter than internal diameter of ducts.

    - Grounding: Test manhole grounding to ensure electrical continuity of bonding and grounding connections. Measure ground resistance at each ground rod and report results. Use an instrument specifically designed for ground-resistance measurements.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Sole Source