READ THIS FIRST

Notice to the Design Engineer; please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Electrical Identification” Work is shown in the Contract Documents.  This section includes identification of electrical materials, equipment, and installations.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ANSI/IEEE C2 - National Electrical Safety Code

    - NFPA 70 (National Fire Protection Association) - National Electrical Code, References

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Samples: For each type of label and sign to illustrate size, colors, lettering style, mounting provisions, and graphic features of identification products.

    - Submittals shall include the following:

      - Product Data for each type of product specified.

      - Schedule of identification nomenclature to be used for identification signs and labels.

  - QUALITY ASSURANCE

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

    - Comply with ANSI C2, ANSI A13.1., ANSI Z535.4, 29 CFR 1910.144 and 29 CFR 1910.145.

    - Comply with Port of Seattle standards for electrical equipment identification.

    - Adhesive-attached labeling materials, including label stocks, laminating adhesives, and inks used by label printers, shall comply with UL 969.

  - COORDINATION

    - Coordinate identification names, abbreviations, colors, and other features with requirements in other Sections requiring identification applications, Drawings, Shop Drawings, manufacturer's wiring diagrams, and the Operation and Maintenance Manual; and with those required by codes, standards, and 29 CFR 1910.145. Use consistent designations throughout Project.

    - Coordinate installation of identifying devices with completion of covering and painting of surfaces where devices are to be applied.

    - Coordinate installation of identifying devices with location of access panels and doors.

    - Install identifying devices before installing acoustical ceilings and similar concealment.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - LABEL TYPES

    - Manufacturer’s standard products with colors prescribed by ANSI A13.1, NFPA 70, and these Specifications. Only temporary markings that are removable without damaging finish are permitted on equipment.

      - Equipment Identification Labels: On each unit of equipment, install unique designation label that is consistent with wiring diagrams, schedules, and the Operation and Maintenance Manual. Install labels and nameplates parallel to equipment lines. Apply labels to disconnect switches and protection equipment, central or master units, control panels, control stations, terminal cabinets, and racks of each system. Systems include power, lighting, control, communication, signal, monitoring, and alarm systems unless equipment is provided with its own identification.

      - Provide engraved laminated phenolic plastic or melamine label for equipment as noted below. Securely attach engraved labels with blunt end, self-tapping stainless steel screws with blunt ends. Sheet metal screws are not allowed. Provide white letters on black background for normal power, white letters on red background for emergency power.

        - Provide 5/8-inch minimum height letters on the following equipment:

          - Panelboards, provide labels and warning signs. Secure nameplates to inside surface of door where panel is recessed in finished locations.

          - Switchboards/distribution centers, motor control centers and power centers, padmounted transformers

          - Secondary feeder breakers in distribution equipment

          - Automatic and manual transfer switches. Labels shall include both normal and emergency source and load.

          - Special equipment housed in cabinets, on outside door

          - Terminal junction boxes and data gathering panels

          - Cable trays

          - UPS equipment

        - Provide 1/4-inch minimum height letters on the following equipment:

          - Disconnects and starters for motors on fixed appliances and starters in MCCs

          - Motor controllers and VFDs.

          - Enclosed switches and circuit breakers

          - Low voltage transformers

          - Feeder circuit breakers in switchboards, switchgear, and distribution panelboards. Circuit breakers shall be labeled with destination panel name or load.

          - Duplex receptacles (self adhesive labels indicating panel and circuit number)

          - Local control panels

          - Raceways and junction boxes

          - Instrumentation Labels

        - Refer to table and descriptions in subparagraphs below for acceptable labeling procedure:

Verify label and letter size will fit the actual space available

| SECTION | TITLE | LABEL TYPES |
| --- | --- | --- |

|  |  | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 26 05 26 | Grounding |  |  | ⅝ |  | X |  |  |  |  |  |  |  |  |  |  |  |
| 26 05 23 | Control/Signal Transmission Media | X | X |  |  |  |  |  |  |  |  |  |  |  | X |  |  |
| 26 05 19 | 600-Volt or Less Wire and Cable | X | X |  |  | X |  |  |  |  |  |  |  |  | X |  |  |
| 26 05 13 | Medium-Voltage Cables |  |  |  |  |  | X |  |  |  |  |  |  |  | X |  |  |
| 26 05 33 | Raceways and Boxes |  |  |  |  |  |  |  |  |  |  |  |  |  |  | X |  |
| 26 05 43 | Underground Ducts and Manholes |  |  |  |  |  | X |  | X | X | X | X |  |  | X |  |  |
| 26 27 16 | Cabinets and Enclosures |  |  | ⅜ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 05 36 | Cable Trays |  |  | ⅜ |  |  |  |  |  |  | X | X |  |  |  |  |  |
| 26 27 26 | Wiring Devices |  |  |  | ¼ |  |  |  |  |  |  |  |  |  |  |  |  |
| no section | Electrical Power Monitoring and Control |  |  | ⅜ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 32 29 | Rotary 400 HZ Converters |  |  | ½ |  |  |  |  |  |  | X |  |  |  |  |  |  |
| 26 32 13 | Engine Generators |  |  | ⅝ |  |  |  |  |  |  | X |  |  |  |  |  |  |
| 26 33 53 | Static Uninterruptible Power Supplies |  |  | ⅝ |  |  |  |  |  |  | X |  |  |  |  |  |  |
| 26 29 23 | Variable Frequency Controllers |  |  | ⅝ |  |  |  |  |  |  | X |  |  |  |  |  |  |
| 26 12 00 | Medium-Voltage Transformers |  |  | ⅝ |  |  |  |  |  |  | X |  | X |  |  |  |  |
| 26 35 33 | Low-Voltage Power Factor Correction Capacitors |  |  | ⅜ | X |  |  |  |  |  |  |  | X |  |  |  |  |
| 26 13 00 | Medium-Voltage Load Interrupter Switchgear |  |  | ⅝ |  |  |  |  |  |  | X |  | X |  |  |  |  |
| 26 13 26 | Medium-Voltage Metal-Clad Drawout Circuit Breaker Switchgear |  |  | ⅝ |  |  |  |  |  |  | X |  | X |  |  |  |  |
| 26 18 39 | Medium-Voltage Motor Controllers |  |  | ⅝ |  |  |  |  |  |  | X |  | X |  |  |  |  |
| 26 13 19 | Medium-Voltage Pad-Mounted Vacuum Interrupter Switchgear |  |  | ⅝ |  |  |  |  |  |  | X |  | X |  |  |  |  |
| 26 11 16 | Secondary Unit Substations |  |  | ⅝ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 28 16 | Enclosed Switches and Circuit Breakers |  |  | ⅝ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 36 00 | Transfer Switches |  |  | ⅝ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 23 00 | Low-Voltage Switchgear |  |  | ⅝ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 24 13 | Low-Voltage Switchboards |  |  | ⅝ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 09 26 | Panelboards |  |  | ½ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 24 19 | Motor-Control Centers |  |  | ⅝ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 29 13 | Motor Controllers |  |  | ⅜ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 25 00 | Low-Voltage Busway |  |  | ⅜ |  |  |  |  |  |  |  | X | X |  |  |  |  |
| 26 22 00 | Dry-Type Transformers (600-Volt and Less) |  |  | ½ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 28 13 | Fuses |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 43 13 | Transient Voltage Suppression |  |  | ⅜ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 51 00 | Interior Lighting |  |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 56 00 | Exterior Lighting |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 09 23 | Lighting Controls |  |  | ½ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 28 31 00 | Fire Alarm |  |  | ½ |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 08 00 | Acceptance Testing |  |  |  |  |  |  |  |  |  |  |  |  | X |  |  |  |

    - Heat-shrink preprinted tubes, flame-retardant polyolefin tube with machine-printed identification label.  Sized to suit diameter of and shrinks to fit firmly around cable it identifies.  Full shrink recovery at a maximum of 200 degree F.  Comply with UL 224.

    - Preprinted, flexible, self-adhesive vinyl label laminated with a clear weather- and chemical-resistant coating and matching wraparound clear adhesive tape for securing ends of legend label.

    - Engraved melamine plastic laminate flat stock, 1/16-inch minimum thickness for sizes up to 15 square inches. Use 1/8-inch minimum for sizes larger than 15 square inches. Black with white letters for normal power systems and red with white letters for emergency power systems, with height as shown in table above unless specified otherwise. UV-inhibited when used outdoors. Secure with stainless steel drive screws, stainless steel self-tapping screws or stainless steel oval-head 6-32 screws tapped into enclosure, or with stainless steel bolts with elastic stopnut.

    - Adhesive-backed plastic machine-printed labels, white with black letters.  Indicate panel name and circuit number(s).

      - For Raceway at more than 600V, provide black letters on an orange field label with the legend, “HIGH VOLTAGE”.  Indicate feeder number.

    - Plain-colored vinyl adhesive tape, 3-mil minimum by 1-inch wide minimum. Apply 1/2-inch minimum over-wrap through 2-inch minimum length. Refer to Section 26 05 19 – 600 Volt or Less Wire and Cable for color.

    - Engraved plastic melamine laminate flat stock.  1/16 inch minimum thickness for sizes up to and including 15 square inches, 1/8” thick for larger than 15 square inches.  White background with black letters for normal power, red background with white letters for emergency power.  Holes at each end for attachment with nylon ty-wraps.

    - Not used

    - Underground line warning tape with pre-printed warning message identifying type of system. Material shall be pigmented polyolefin, continuous-printed on one side, and compounded for unlimited life when direct buried. 6-inch minimum width by 4-mils thick.   Tensile strength of 1750 psi.

      - Inscriptions for Red-Colored Tapes:  ELECTRICAL LINE, HIGH VOLTAGE.

      - Inscriptions for Orange-Colored Tapes:  TELEPHONE CABLE, CATV CABLE, COMMUNICATION CABLE, OPTICAL FIBER CABLE.

    - Underground metallic line-warning tape with pre-printed warning message identifying type of system. Material shall be detectable three-layer laminate consisting of printed pigmented polyolefin, a solid aluminum-foil core with a clear protective film that allows inspection of the continuity of the conductive core, and compounded for unlimited life when direct buried. Use when metal-detection of line is required on Medium Voltage Systems. 6-inch minimum width by 4-mils thick.

      - Inscriptions for Red-Colored Tapes:  “CAUTION:  MEDIUM VOLTAGE ELECTRICAL LINE BELOW”

    - Warning signs: Baked Enamel on aluminum plate, punched or drilled for fasteners, with colors, legend, and size required for applications. ¼-inch grommets in corners for mounting. Minimum nominal size of 7 by 10 inches with 0.040-inch minimum thickness. OSHA standard wording where approved. Custom wording if required. Secure with non-corrosive fasteners.

      - Where applicable, provide labels for multiple power source warning:  “DANGER – ELECTRICAL SHOCK HAZARD – EQUIPMENT HAS MULTIPLE POWER SOURCES”

    - Warning labels: Self-adhesive, multicolor, flexible pressure-sensitive vinyl conforming to OSHA “Danger” and “Caution” standards. 2½ x1¾” minimum with black letters on yellow background. Label shall read: “WARNING! DO NOT USE AS WALKWAY, LADDER, OR SUPPORT FOR LADDERS OR PERSONNEL - CABLES ADDED AFTER INITIAL INSTALLATION REQUIRE POS/F & I APPROVAL.” See Section 26 05 36 – Cable Trays

      - Where applicable, provide labels for multiple power source warning:  “DANGER – ELECTRICAL SHOCK HAZARD – EQUIPMENT HAS MULTIPLE POWER SOURCES”

    - Stencils: Machine-punched patterns, nonfading waterproof paint with color and formulation appropriate for material and location. Minimum letter height shall be 1 inch.

    - Adhesive-backed metal labels manufactured with testing agency logo. Punched or engraved with actual settings and date.  Label shall be 1/16-inch minimum thickness for sizes up to 15 square inches. Use 1/8-inch minimum for sizes larger than 20 square inches.   Black with white letters for normal power systems and red with white letters for emergency power systems, with height as shown in table above unless specified otherwise.

    - Stainless-steel machine or hand-stamped wire marker plates with one hole at each end for attachment with non-corrosive fasteners that do 0.010-inch minimum thickness (for outdoor application).

    - Adhesive machine-printed plastic tape, cut to length, black with white letters unless specified otherwise. 3/8-inch minimum width of tape in unfinished areas only. Provide white lettering on red background when served by an emergency source.

  - MISCELLANEOUS IDENTIFICATION PRODUCTS

    - Floor Marking:  Coordinate with the Port Electric Shop for painting working clearances on the floor in front of the equipment.

    - Paint:  Comply with requirements in painting Sections for paint materials and application requirements.  Select paint system applicable for surface material and location (exterior and interior).

- EXECUTION

  - INSTALLATION

    - Fasteners for labels and signs: Self tapping, blunt-ended stainless-steel screws, or stainless-steel machine screws with nuts and flat and lock washers. Sheet metal screws are not acceptable. Self-drilling screws are not allowed.

    - Install identification labels according to manufacturer’s written instructions.

    - Install labels where indicated and as required by the Authority Having Jurisdiction and the Department of Labor and Industries. Locate for optimum viewing and without interference with the operation and maintenance of equipment.

    - Verify identity of each item before installing identification products.

    - Labeling abbreviations not permitted without F&I approval.

    - Temporary markings allowed only if removable without damage to equipment or enclosure finish.

    - System Identification Color-Coding Bands for Raceways: Each color-coding band shall completely encircle cable or conduit. Place adjacent bands of two-color markings in contact, side by side. Locate bands at changes in direction, at penetrations of walls and floors, at 50-foot (15-m) maximum intervals in straight runs, and at 25-foot (7.6-m) maximum intervals in congested areas.

      - 208/120V	Blue

      - 480/277V	Yellow

      - Controls	Black

    - Cable Ties: For attaching tags. Use general-purpose type, fungus inert, self-extinguishing, one piece, self-locking Type 6/6 nylon, except as listed below:

      - Outdoors: UV-stabilized nylon.

      - In spaces handling environmental air: Plenum rated.

    - Underground-Line Warning Tape: During backfilling of trenches install continuous underground-line warning tape directly above line at 6 to 8 inches below finished grade. Use multiple tapes where width of multiple lines installed in a common trench or concrete envelope exceeds 16 inches overall.

    - Coordinate names, abbreviations, colors, graphics and other designations used for electrical identification with corresponding designations used in the Contract Documents or as required by codes and standards. Use consistent designations throughout the Project. Labeling abbreviations are not allowed.

    - Sequence of Work: Where identification is to be applied to surfaces that require finish, install identification after completion of finish Work.

      - Coordinate installing electrical identifying labels prior to installing acoustical ceilings and similar finishes that conceal such items.

    - Clean surfaces of dust, loose material, and oily films before applying painted or self-adhesive identification products.

    - Painted Identification Products:

      - Prime surfaces according to manufacturer’s instructions prior to applying painted labels:

        - For galvanized metal, use single-component, acrylic vehicle coating formulated for galvanized surfaces.

        - For concrete masonry units, use heavy-duty, acrylic-resin block filler.

        - For concrete surfaces, use clear, alkali-resistant, alkyd binder-type sealer.

      - Apply one intermediate and one finish coat of paint.

  - IDENTIFICATION SCHEDULE

    - Panelboard Schedules:

      - Panelboard schedules shall utilize the POS standard panel schedule in Microsoft Excel format which has provision for totaling all loads and performing demand calculations by load category.

      - Electronic copies of schedules are available from the Facilities and Infrastructure department. The STIA standard template is available on the Port of Seattle internet site, included with the STIA Electrical Standards.  http://www.portseattle.org/Business/Construction-Projects/Airport-Tenants/Pages/Reference-Documents.aspx.

      - This schedule shall be updated with as-built information upon the completion of the project. The contractor shall post a hard copy of the revised panel schedule in any panel modified and submit an electronic copy of the panel schedule in Port standard excel format showing accurate as-built information to F&I.

    - Instrumentation Labels: Affix permanent type nameplate or tag on all field-mounted instruments, transmitters, pressure gauges, and control valves with proper identification number and service description.

      - Provide 3”x1” aluminum or stainless steel tag stamped with the instrument loop number designation and the calibrated range.

    - Medium Voltage Raceways: Provide 5/8 inch high stenciled or manufactured letters noting “HIGH VOLTAGE”, black letters on yellow background on all exposed feeder conduits where entering or leaving switchboards and along conduit runs at 25 feet on center.

    - Accessible Raceways, More Than 600 V: Self-adhesive vinyl labels. Install labels at all conduit penetrations and along length of exposed conduit run at 25 foot maximum intervals.

    - Accessible Raceways within Buildings: Identify the covers of each junction and pull box of the following systems with self-adhesive vinyl labels with the wiring system legend and system voltage.

      - Provide labels on all raceways, junction and pull boxes indicating panel designation and circuit number for all circuits in raceway or box, and conduit destination.

        - Conduit Label Example: B2-P4-23G-1/1,3,5, B-2601-9.

        - Provide labels at all locations where conduit penetrates walls, floors and ceilings, on both sides of penetration.

        - Provide labels at all ends or breaks in conduit runs such as electrical rooms, junction boxes, pull boxes, cabinets, maintenance holes, fire penetrations, etc.

        - Provide labels on each conduit entering junction or pull box within 12” of junction or pull box.

        - Provide labels at 25 foot maximum intervals along conduit runs.

        - Provide labels on all junction and pullboxes, including in accessible ceiling spaces and exposed in unfinished areas. Refer to specification sections for identification requirements for systems contained within.

        - Install labels parallel to equipment lines.

        - Labels in unfinished locations, including in accessible ceiling spaces and exposed unfinished areas shall be machine printed vinyl labels minimum ½ inch high, white with black letters. Labels in finished locations shall be adhesive-backed plastic machine printed labels, minimum 3/8 inch high, white with black letters.

        - Lettering shall be a minimum of ¼” high.

        - In finished locations, provide labels on inside of junction or pull box cover.

        - Provide red lettering when served by an emergency source.

    - Power-Circuit Conductor Identification, 600 V or Less: For conductors in vaults, pull and junction boxes, manholes, and handholes, use color-coding conductor tape to identify the phase.

      - Color-Coding for Phase and Voltage Level Identification, 600 V or Less: Use colors listed below for feeder and branch-circuit conductors.

        - Provide colored insulation when available, typically for wire sized #8 AWG and smaller.

        - Provide minimum 2 inch wide band of colored plastic tape at all terminations and splices (where allowed). 3M Scotch No. 35, [        ], Or Approved Equal Electrical Color Coding Tape.

        - Colors for 480/277V 3Ø, 4-wire systems:

          - Phase A (left or top): 		Brown.

          - Phase B (center): 		Orange

          - Phase C (right or bottom):	Yellow

          - Neutral:			Gray

          - Ground:			Green

        - Colors for 208/120V, 3Ø, 4-wire systems:

          - Phase A (left or top):		Black

          - Phase B (center): 		Red

          - Phase C (right or bottom): 	Blue

          - Neutral:			White

          - Ground:			Green

          - Isolated Ground:		Green with yellow or orange stripe

        - 575V, 3Ø, 4-wire systems

          - Phase A (left or top):		Brown with purple stripe

          - Phase B (center): 		Orange with purple stripe

          - Phase C (right or bottom): 	Yellow with purple stripe

          - Neutral:			Gray with purple stripe

          - Ground:			Green

        - Colors for 120/240V, 1Ø, 3-wire systems: (non-standard)

          - Phase A:			Black

          - Phase B:			Red

          - Neutral:			White

          - Ground:			Green

        - For 240-delta systems (obsolete) the color of the high leg (approximately 200 volts to ground) shall be red. Label interior of all equipment “CAUTION: HIGH LEG IS OVER 120V TO GROUND. DO NOT USE FOR 120V CIRCUITS”.

        - Field-Applied, Color-Coding Conductor Tape: Apply in half-lapped turns for a minimum distance of 6 inches from terminal points and in boxes where splices or taps are made. Apply last two turns of tape with no tension to prevent possible unwinding. Locate bands to avoid obscuring factory cable markings.

      - Provide wire markers on each conductor in panelboards, gutters, pull boxes, outlet and junction boxes and at the load connection. Identify with branch circuit or feeder number for power and lighting circuits.

        - Install conductor labeling in panelboards and enclosures to ensure labels are visible.

    - Power-Circuit Conductor Identification, Medium Voltage: Provide labeling at all accessible locations including each termination or interconnection of wiring, and in vaults, pull and junction boxes, manholes, and handholes. Identify conductors with cloth type, split sleeve or tubing type wire and cable markers.

      - Label each cable with phase designation, operating voltage and circuit number.

      - Color Coding for Phase:

        - 4160Y/2400V AC 3Ø, 4-wire:

          - Phase A:		Black/Pink

          - Phase B:		Red/Pink

          - Phase C:		Blue/Pink

          - Neutral:		White/Pink

        - 4160V Delta AC, 3Ø, 4-wire

          - Phase A:		Black/Brown

          - Phase B:		Red/Brown

          - Phase C:		Blue/Brown

        - 12,470V Delta AC, 3Ø, 4-wire

          - Phase A:		Black/Orange

          - Phase B:		Red/Orange

          - Phase C:		Blue/Orange

      - Provide write-on tags or nonmetallic plastic tag holder with adhesive-backed phase tags, and a separate tag with the circuit designation.

    - Install instructional sign including the color code for grounded and ungrounded conductors using adhesive-film-type labels.

    - Control-Circuit Conductor Identification: For conductors and cables in pull and junction boxes, manholes, and handholes, use self-adhesive vinyl labels with the conductor or cable designation, origin, and destination.

      - Provide wire markers on each conductor in wire gutters, pull boxes, outlet and junction boxes and at the equipment connection. Identify with control wire number as indicated on schematics and interconnection diagrams or equipment manufacturer’s shop drawings for control wiring.

    - Control-Circuit Conductor Termination Identification: For identification at terminations provide heat-shrink preprinted tubes with the conductor designation

    - Auxiliary Electrical Systems Conductor Identification: Identify field-installed alarm, control, and signal connections.

      - Identify conductors, cables, and terminals in enclosures and at junctions, terminals, and pull points. Identify by system and circuit designation.

      - Use system of marker tape designations that is uniform and consistent with system used by manufacturer for factory-installed connections.

      - Coordinate identification with Project Drawings, manufacturer's wiring diagrams, and the Operation and Maintenance Manual.

    - Conductor Identification:

      - Conductors to Be Extended in the Future: Indicate source and circuit numbers.

      - Multiple Power or Lighting Circuits in the Same Enclosure: Identify each conductor with source, voltage, circuit number, and phase. Use color coding for voltage and phase indication of secondary circuit.

      - Multiple Control and Communications Circuits in the Same Enclosure: Identify each conductor by its system and circuit designation. Use a consistent system of tags, color coding, or cable marking tape.

    - Locations of Underground Lines: Identify with underground-line warning tape for power, lighting, communication, and control wiring and optical fiber cable.

      - Install underground-line warning tape for both direct-buried cables and cables in raceway.

    - Workspace Indication: Install floor marking tape or paint to show working clearances in the direction of access to live parts. Workspace shall be as required by NFPA 70 and 29 CFR 1926.403 unless otherwise indicated. Do not install at flush-mounted panelboards and similar equipment in finished spaces.

    - Warning, Caution, and Instruction Signs:

      - Install warning, caution, and instruction signs where indicated or required to ensure safe operation and maintenance of electrical systems and of items to which they connect. Provide OSHA standard text where approved. Provide text of sufficient clarity and lettering of sufficient size to convey adequate information at each location. Mount permanently in an appropriate location. Comply with ANSI A13.1 standard color and design.

      - Operating Instruction Signs: Install instruction signs to facilitate proper operation and maintenance of electrical systems and items to which they connect. Install instruction signs with approved legend where instructions are needed for system or equipment operation.

      - Emergency-Operating Signs: Install engraved laminate signs with white legend on red background with minimum 3/8-inch high lettering for emergency instructions on power transfer, load shedding, and other emergency operations.

    - Apply equipment identification labels of engraved plastic laminate on each major unit of equipment, including central or master unit of each system. This includes communication, signal, and alarm systems, unless units are specified with their own self-explanatory identification. Except as otherwise indicated, provide a single line of text with 1/4-inch high lettering on 1-inch high label. Use white lettering on black field. Apply labels parallel to equipment lines.

    - Outdoor Equipment: Engraved, laminated acrylic or melamine label, to comply with requirements listed above. Provide panel schedule printed on 8.5x11 paper in Port standard format in each panelboard. Insert folded schedule in schedule holder on inside of panel door. Posted panel schedule shall be updated to reflect all new work in panel. Include project completion date on schedule.

    - Provide self-adhesive tape labels on all receptacle cover plates.  Labels shall be machine printed with black lettering on white or clear background.

      - Indicate source panel name and circuit number.

      - Provide red lettering on white or clear background for devices on emergency circuits.

      - Where receptacle faceplate is dark color, provide white letters on clear background.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2, and revisions

01/29/2015 Revised Four Section Numbers that had changed and Sole Source

09/13/2016 Added missing details from F&I section 260553

02/08/2018 Updated Table.