READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab). You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent of “Short Circuit, Coordination, and Arc Flash Study” Work is shown in the Contract Documents. This section includes requirements for furnishing a report on short-circuit and protective device coordination and breaker coordination studies, and an arc flash hazard analysis study. The study should be conducted by the design Engineer at the initial of the design of the project, It will be repeated by the Contractor during the initial shop drawings submittal phase of the contract and at the final as-built stage of the contract, ( total of three times).

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - NFPA 70 (National Fire Protection Association) - National Electrical Code.

    - IEEE 141 – Recommended Practice for Electric Power Distribution and Coordination of Industrial and Commercial Power Systems

    - IEEE 242 – Recommended Practice for Protection and Coordination of Industrial and Commercial Power Systems

    - IEEE 399 – Recommended Practice for Industrial and Commercial Power System Analysis

    - IEEE 241 – Recommended Practice for Electric Power Systems in Commercial Buildings

    - IEEE 1015 – Recommended Practice for Applying Low Voltage Circuit Breakers Used in Industrial and Commercial Power Systems

    - IEEE 1584 – Guide for Performing Arc-Flash Hazard Calculations

    - ANSI C57.12.00 (American National Standards Institute) – Standard General Requirements for Liquid-Immersed Distribution, Power, and Regulating Transformers

    - ANSI C37.13 – Standard for Low Voltage AC Power Circuit Breakers Used in Enclosures

    - ANSI C37.010 – Standard Application Guide for AC High Voltage Circuit Breakers Rated on a Symmetrical Current Basis

    - ANSI C 37.41 – Standard Design Tests for High Voltage Fuses, Fuse and Disconnecting Cutouts, Distribution Enclosed Single-Pole Air Switches, and Fuse Links and Accessories Used with These Devices.

    - NFPA 70E – Standard for Electrical Safety in the Workplace

  - SUBMITTALS

    - The short-circuit and protective device coordination studies shall be submitted to the design Engineer prior to receiving final approval of the distribution equipment shop drawings and/or prior to release of equipment drawings for manufacturing. If formal completion of the studies may cause delay in equipment manufacturing, approval from the Engineer shall be obtained for preliminary submittal of sufficient study data to ensure that the selection of device and characteristics will be satisfactory.

    - The results of the short-circuit, protective device coordination and arc flash hazard analysis studies shall be summarized in a final report; signed dated, and sealed by a Professional Electrical Engineer licensed in the State of Washington. No more than five (5) bound copies of the complete final report shall be submitted. For large system studies, submittals requiring more than five (5) copies of the report will be provided without the section containing the computer printout of the short-circuit input and output data. Additional copies, where required, shall be provided on CD in PDF format.

    - The report shall include the following sections:

      - One-line diagram showing protective device ampere ratings and associated designations, cable size & lengths, transformer kVA & voltage ratings, motor & generator kVA ratings, and switchgear/switchboard/panelboard designations.

      - Descriptions, purpose, basis and scope of the study.

      - Tabulations of the worst-case calculated short circuit duties as a percentage of the applied device rating (automatic transfer switches, circuit breakers, fuses, etc.); the short circuit duties shall be upward-adjusted for X/R ratios that are above the device design ratings.

      - Protective device time versus current coordination curves with associated one line diagram identifying the plotted devices, tabulations of ANSI protective relay functions and adjustable circuit breaker trip unit settings.

      - Fault study input data, case descriptions, and current calculations including a definition of terms and guide for interpretation of the computer printout.

      - Incident energy and flash protection boundary calculations.

      - Comments and recommendations for system improvements, where needed.

      - Executive Summary including source of information and assumptions made.

    - Operation and Maintenance Data: For the overcurrent protective devices to include in emergency, operation, and maintenance manuals.

      - In addition to items specified in Section 01 78 23.13 - Operations and Maintenance Data, include the following:

        - The following parts from the Protective Device Coordination Study Report:

          - One-line diagram.

          - Protective device coordination study.

          - Time-current coordination curves.

        - Power system data.

      - Maintenance procedures according to requirements in NFPA 70E shall be provided in the equipment manuals.

    - Power System Equipment Database (PSDB) shall be provided to the owner at the completion of the study.  The database shall contain and list all electrical equipment used in the study and the results of the short circuit, protective device study, and arc flash study. The data base shall have the minimum features and functions:

      - Equipment Nameplate Data and Protective Device Settings for the equipment listed below:

        - ATS

        - Circuit Breakers

        - Motor Control Centers

        - Bus Duct Runs

        - Relays

        - Transformers

        - Conductors

        - Control Panels

        - Fuses

        - Motor Starters

        - Panelboards

        - Switchboards

        - Switchgear

        - Disconnect Switches

        - Generators

        - Motors > 50HP

        - PDUs

        - VFDs

        - Utility Data

        - Other equipment as identified by POS or Engineer of record.

      - The equipment nameplate data shall include a minimum of the following information:

        - Manufacturer

        - Type

        - Voltage

        - Amperage

        - kVA

        - HP

        - Size and Length (conductor)

        - # per phase (conductor)

        - RLA & LRA (motor)

        - NEMA code (motor)

        - Frame Size

        - Trip

        - Sensor

        - Breaker and Relay Settings

        - Impedance (generators and transformers)

        - Winding Connections (transformers)

        - Temperature rating

        - Short Circuit Rating

        - Withstand rating

        - Date of manufacture

        - Weight (transformers)

        - Catalog number and serial number

  - QUALITY ASSURANCE

    - Studies shall use computer programs that are distributed nationally and are in wide use. Software algorithms shall comply with requirements of standards and guides specified in this section. Manual calculations are unacceptable.

    - Coordination Study Software Developer Qualifications: An entity that owns and markets computer software used for studies, having performed successful studies of similar magnitude on electrical distribution systems using similar devices.

      - The computer program shall be developed under the charge of a Professional Engineer licensed in the State of Washington who holds IEEE Computer Society's Certified Software Development Professional certification.

    - Coordination Study Specialist Qualifications: Professional Engineer in charge of performing the study and documenting recommendations, licensed in the State of Washington who has at least ten (10) years of experience and specializes in performing power system studies.  All elements of the study shall be performed under the direct supervision and control of this Professional Engineer.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - COMPUTER SOFTWARE DEVELOPERS

    - Comply with IEEE 242 and IEEE 399.

    - Perform studies with one of the following software:

      - ETAP

      - EasyPower

      - SKM, Inc.

      - Or Approved Equal.

  - STUDIES

    - Contractor to furnish short-circuit and protective device coordination studies as prepared by equipment manufacturer. By using the equipment manufacturer the study allows coordination of proper breakers, fuses, and current transformers. The coordination study shall begin with the utility company's feeder protective device and include all of the electrical protective devices down to and include the largest feeder circuit breaker and motor starter in the 480 Volt motor control centers and power distribution panelboards. The study shall also include variable frequency drives, harmonic filters, power factor correction equipment, transformers and protective devices associated with variable frequency drives, emergency and standby generators associated paralleling equipment and distribution switchgear.

    - The Contractor shall furnish an Arc Flash Hazard Analysis Study per NFPA 70E - Standard for Electrical Safety in the Workplace, reference Article 130.3 and Annex D.

  - DATA COLLECTION

    - Contractor shall furnish all field data as required by the power system studies. The Contractor performing the short-circuit, protective device coordination and arc flash hazard analysis studies shall furnish and submit to POS a list of required data immediately after award of the contract. The Contractor shall expedite collection of the data to eliminate unnecessary delays and assure completion of the studies as required for final approval of the distribution equipment shop drawings and/or prior to the release of the equipment for manufacturing.

    - Source combination may include present and future utility supplies, motors, and generators.

    - Load data utilized may include existing and proposed loads obtained from Contract Documents provided by POS.

    - Include fault contribution of existing motors in the study, with motors < 50 hp grouped together. The Contractor shall obtain required existing equipment data, if necessary, to satisfy the study requirements.

  - SHORT-CIRCUIT AND PROTECTIVE DEVICE EVALUATION STUDY

    - Use actual conductor impedances if known. If unknown, use typical conductor impedances based on IEEE Standards 141, latest edition.

    - Transformer design impedances and standard X/R ratios shall be used when test values are not available.

    - Provide the following:

      - Calculation methods and assumptions

      - Selected base per unit quantities

      - One-line diagram of the system being evaluated with available fault at each bus, and interrupting rating of devices noted

      - Source impedance data, including electric utility system and motor fault contribution characteristics

      - Typical calculations

      - Tabulations of calculated quantities

      - Results, conclusions, and recommendations

    - Provide report on short-circuit momentary and interrupting duties for a three-phase and unbalanced fault calculations at each of the device location listed below. For each device, the reports shall include, but not limited to, the device’s voltage, calculated fault-current magnitude and angle, fault-point X/R ratio, calculated asymmetrical fault currents, and impedances.

      - Electric utility’s supply termination point

      - Incoming switchgear

      - Unit substation primary and secondary terminals

      - Low voltage switchgear

      - Motor control centers

      - Standby generators and automatic transfer switches

      - Branch circuit panelboards

      - Other significant locations throughout the system

    - For grounded systems, provide a bolted line-to-ground fault current study for areas as defined for the three-phase bolted fault short-circuit study.

    - Protective Device Evaluation:

      - Evaluate equipment and protective devices and compare to short circuit ratings

      - Adequacy of switchgear, motor control centers, and panelboard bus bracing to withstand short-circuit stresses

      - Adequacy of transformer windings to withstand short-circuit stresses

      - Cable and busway sizes for ability to withstand short-circuit heating

      - Notify Engineer in writing, of existing, circuit protective devices improperly rated for the calculated available fault current

  - PROTECTIVE DEVICE COORDINATION STUDY

    - Proposed protective device coordination time-current curves shall be graphically displayed on log-log scale paper.

    - Include on each curve sheet a complete title and one-line diagram with legend identifying the specific portion of the system covered.

    - Terminate device characteristic curves at a point reflecting maximum symmetrical or asymmetrical fault current to which device is exposed.

    - Identify device associated with each curve by manufacturer type, function, and, if applicable, tap, time delay, and instantaneous settings recommended.

    - Plot the following characteristics on the curve sheets, where applicable:

      - Electric utility’s protective device

      - Medium voltage equipment overcurrent relays

      - Medium and low voltage fuses including manufacturer’s minimum melt, total clearing, tolerance, and damage bands

      - Low voltage equipment circuit breaker trip devices, including manufacturer’s tolerance bands

      - Transformer full-load current, magnetizing inrush current, and ANSI transformer withstand parameters

      - Conductor damage curves

      - Ground fault protective devices, as applicable

      - Pertinent motor starting characteristics and motor damage points

      - Pertinent generator short-circuit decrement curve and generator damage point

      - Other system load protective devices for the largest branch circuit and the largest feeder circuit breaker in each motor control center

    - Provide adequate time margins between device characteristics such that selective operation is provided, while providing proper protection.

  - ARC FLASH HAZARD ANALYSIS

    - The arc flash hazard analysis shall be performed according to the IEEE 1584 equations that are presented in NFPA70E (current edition), Annex D.

    - When appropriate, the short circuit calculations and the clearing times of the phase overcurrent devices will be retrieved from the short-circuit and coordination study model. Alternative methods shall be presented in the proposal.

    - The flash protection boundary and the incident energy shall be calculated at all significant locations in the electrical distribution system (switchboards, switchgear, motor-control centers, panelboards, busway and splitters) where work could be performed on energized parts.

    - The Arc-Flash Hazard Analysis shall include all medium voltage, 600V, & 480V locations and significant locations in 240 volt and 208 volt systems fed from transformers equal to or greater than 125 kVA.

    - Safe working distances shall be specified for calculated fault locations based upon the calculated arc flash boundary considering incident energy of 1.2 cal/cm2.

    - The Arc Flash Hazard analysis shall include calculations for maximum and minimum contributions of fault current magnitude. The minimum calculation shall assume that the utility contribution is at a minimum and shall assume a minimum motor load. Conversely, the maximum calculation shall assume a maximum contribution from the utility and shall assume motors to be operating under full-load conditions.

    - Arc flash computation shall include both line and load side of main breaker calculations, where necessary.

    - Arc Flash calculations shall be based on actual overcurrent protective device clearing time. Maximum clearing time will be capped at 2 seconds based on IEEE 1584-2002 section B.1.2.

  - REPORT SECTIONS

    - Input Data:

      - Utility three-phase and line-to-ground available contribution with associated X/R ratios

      - Short-circuit reactance of rotating machines with associated X/R ratios

      - Cable type, construction, size, # per phase, length, impedance and conduit type

      - Bus duct type, size, length, and impedance

      - Transformer primary & secondary voltages, winding configurations, kVA rating, impedance, and X/R ratio

      - Reactor inductance and continuous ampere rating

      - Aerial line type, construction, conductor spacing, size, # per phase, and length

    - Short-Circuit Data: Interrupting Duty Report: Three-phase and unbalanced fault calculations, showing the following for each overcurrent device location:

      - Voltage

      - Source fault impedance and generator contributions

      - X to R ratios

      - Asymmetry factors

      - Motor contributions

      - Short circuit kVA

      - Symmetrical and asymmetrical fault currents

    - Recommended Protective Device Settings:

      - Phase and Ground Relays:

        - Current transformer ratio.

        - Current setting.

        - Time setting.

        - Instantaneous setting.

        - Specialty non-overcurrent device settings.

        - Recommendations on improved relaying systems, if applicable.

      - Circuit Breakers:

        - Adjustable pickups and time delays (long time, short time, ground).

        - Adjustable time-current characteristic.

        - Adjustable instantaneous pickup.

        - Recommendations on improved trip systems, if applicable.

    - Incident energy and flash protection boundary calculations. Provide summary report for each device in study, with list of all “Dangerous” locations (using maximum calculated energy levels) where the incident energy level is 40 cal/cm2, above Hazard Risk Category 4. The report shall list the following items:

      - Bus Name

      - Upstream Protective Device Name, Type, and Settings

      - Bus Line-to-Line Voltage

      - Bus Bolted Fault Current

      - Protective Device Bolted Fault Current

      - Arcing fault magnitude

      - Device clearing time

      - Duration of arc

      - Arc flash boundary

      - Working distance

      - Incident energy

      - Hazard Risk Category

      - Recommendations for arc flash energy reduction

- EXECUTION

  - POWER SYSTEM DATA

    - Obtain all data necessary for the conduct of the overcurrent protective device study.

      - Verify completeness of data supplied in the one-line diagram on Drawings. Call discrepancies to the attention of Architect.

      - For new equipment, use characteristics submitted under the provisions of action submittals and information submittals for this Project.

      - For existing equipment, whether or not relocated obtain required electrical distribution system data by field investigation and surveys, conducted by qualified technicians and Engineers. The qualifications of technicians and Engineers shall be qualified as defined by NFPA 70E.

      - Existing Equipment Data will be provided by the Port.

    - Gather and tabulate the following input data to support coordination study. The list below is a guide. Comply with recommendations in IEEE 241 and IEEE 551 for the amount of detail required to be acquired in the field. Field data gathering shall be under the direct supervision and control of the Engineer in charge of performing the study, and shall be by the Engineer or its representative who holds NETA certification acceptable to AHJ and Port of Seattle.

      - Product Data for overcurrent protective devices specified in other Sections and involved in overcurrent protective device coordination studies. Use equipment designation tags that are consistent with electrical distribution system diagrams, overcurrent protective device submittals, input and output data, and recommended device settings.

      - Electrical power utility impedance at the service. Assume infinite bus for utility power supply.

      - Power sources and ties.

      - Short-circuit current at each system bus, three phase and line-to-ground.

      - Full-load current of all loads.

      - Voltage level at each bus.

      - For transformers, include kVA, primary and secondary voltages, connection type, impedance, X/R ratio, taps measured in percent, and phase shift.

      - For reactors, provide manufacturer and model designation, voltage rating, and impedance.

      - For circuit breakers and fuses, provide manufacturer and model designation. List type of breaker, type of trip and available range of settings, SCCR, current rating, and breaker settings.

      - Generator short-circuit current contribution data, including short-circuit reactance, rated kVA, rated voltage, and X/R ratio.

      - For relays, provide manufacturer and model designation, current transformer ratios, potential transformer ratios, and relay settings.

      - Maximum demands from service meters.

      - Busway manufacturer and model designation, current rating, impedance, lengths, and conductor material.

      - Motor horsepower and NEMA MG 1 code letter designation.

      - Low-voltage cable sizes, lengths, number, conductor material, and conduit material (magnetic or nonmagnetic).

      - Medium-voltage cable sizes, lengths, conductor material, and cable construction and metallic shield performance parameters.

      - Data sheets to supplement electrical distribution system diagram, cross-referenced with tag numbers on diagram, showing the following:

        - Special load considerations, including starting inrush currents and frequent starting and stopping.

        - Transformer characteristics, including primary protective device, magnetic inrush current, and overload capability.

        - Motor full-load current, locked rotor current, service factor, starting time, type of start, and thermal-damage curve.

        - Generator thermal-damage curve.

        - Ratings, types, and settings of utility company's overcurrent protective devices.

        - Special overcurrent protective device settings or types stipulated by utility company.

        - Time-current-characteristic curves of devices indicated to be coordinated.

        - Manufacturer, frame size, interrupting rating in amperes rms symmetrical, ampere or current sensor rating, long-time adjustment range, short-time adjustment range, and instantaneous adjustment range for circuit breakers.

        - Manufacturer and type, ampere-tap adjustment range, time-delay adjustment range, instantaneous attachment adjustment range, and current transformer ratio for overcurrent relays.

        - Panelboards, switchboards, motor-control center ampacity, and SCCR in amperes rms symmetrical.

        - Identify series-rated interrupting devices for a condition where the available fault current is greater than the interrupting rating of the downstream equipment. Obtain device data details to allow verification that series application of these devices complies with NFPA 70 and UL 489 requirements.

  - SHORT CIRCUIT STUDY

    - Gather and tabulate the following input data to support the short-circuit study. Comply with recommendations in IEEE 551 as to the amount of detail that is required to be acquired in the field. Field data gathering shall be under the direct supervision and control of the Engineer in charge of performing the study, and shall be by the Engineer or its representative who holds NETA ETT Level III certification or NICET Electrical Power Testing Level III certification.

      - Product Data for Project's overcurrent protective devices involved in overcurrent protective device coordination studies. Use equipment designation tags that are consistent with electrical distribution system diagrams, overcurrent protective device submittals, input and output data, and recommended device settings.

      - Obtain electrical power utility impedance at the service.

      - Power sources and ties.

      - For transformers, include kVA, primary and secondary voltages, connection type, impedance, X/R ratio, taps measured in percent, and phase shift.

      - For reactors, provide manufacturer and model designation, voltage rating, and impedance.

      - For circuit breakers and fuses, provide manufacturer and model designation. List type of breaker, type of trip, SCCR, current rating, and breaker settings.

      - Generator short-circuit current contribution data, including short-circuit reactance, rated kVA, rated voltage, and X/R ratio.

      - Busway manufacturer and model designation, current rating, impedance, lengths, and conductor material.

      - Motor horsepower and NEMA MG 1 code letter designation.

      - Cable sizes, lengths, number, conductor material and conduit material (magnetic or nonmagnetic).

    - Perform study following the general study procedures contained in IEEE 399.

    - Calculate short-circuit currents according to IEEE 551.

    - Base study on the device characteristics supplied by device manufacturer.

    - The extent of the electrical power system to be studied is indicated on Drawings.

    - Begin short-circuit current analysis at the service, extending down to the system overcurrent protective devices as follows:

      - To normal system low-voltage load buses where fault current is 10 kA or less.

    - Study electrical distribution system from normal and alternate power sources throughout electrical distribution system for Project. Study all cases of system-switching configurations and alternate operations that could result in maximum fault conditions.

    - The calculations shall include the ac fault-current decay from induction motors, synchronous motors, and asynchronous generators and shall apply to low- and medium-voltage, three-phase ac systems. The calculations shall also account for the fault-current dc decrement, to address the asymmetrical requirements of the interrupting equipment.

      - For grounded systems, provide a bolted line-to-ground fault-current study for areas as defined for the three-phase bolted fault short-circuit study.

    - Calculate short-circuit momentary and interrupting duties for a three-phase bolted fault at each of the following:

      - Electric utility's supply termination point.

      - Incoming switchgear.

      - Unit substation primary and secondary terminals.

      - Low-voltage switchgear and distribution panels.

      - Motor-control centers.

      - Control panels.

      - Standby generators and automatic transfer switches.

      - Branch circuit panelboards.

      - Disconnect switches.

  - PROTECTIVE DEVICE COORDINATION STUDY

    - Comply with IEEE 242 for calculating short-circuit currents and determining coordination time intervals.

    - Comply with IEEE 399 for general study procedures.

    - The study shall be based on the device characteristics supplied by device manufacturer.

    - The extent of the electrical power system to be studied is indicated on Drawings.

    - Begin analysis at the service, extending down to the system overcurrent protective devices as follows:

      - To system low-voltage load buses where fault current is 10 kA or less.

    - Study electrical distribution system from normal and alternate power sources throughout electrical distribution system for Project. Study all cases of system-switching configurations and alternate operations that could result in maximum fault conditions.

    - Transformer Primary Overcurrent Protective Devices:

      - Device shall not operate in response to the following:

        - Inrush current when first energized.

        - Self-cooled, full-load current or forced-air-cooled, full-load current, whichever is specified for that transformer.

        - Permissible transformer overloads according to IEEE C57.96 if required by unusual loading or emergency conditions.

      - Device settings shall protect transformers according to IEEE C57.12.00, for fault currents.

    - Motor Protection:

      - Select protection for low-voltage motors according to IEEE 242 and NFPA 70.

      - Select protection for motors served at voltages more than 600 V according to IEEE 620.

    - Conductor Protection: Protect cables against damage from fault currents according to ICEA P-32-382, ICEA P-45-482, and protection recommendations in IEEE 242. Demonstrate that equipment withstands the maximum short-circuit current for a time equivalent to the tripping time of the primary relay protection or total clearing time of the fuse. To determine temperatures that damage insulation, use curves from cable manufacturers or from listed standards indicating conductor size and short-circuit current.

    - Generator Protection: Select protection according to manufacturer's written recommendations and to IEEE 242.

    - The calculations shall include the ac fault-current decay from induction motors, synchronous motors, and asynchronous generators and shall apply to low- and medium-voltage, three-phase ac systems. The calculations shall also account for the fault-current dc decrement, to address the asymmetrical requirements of the interrupting equipment.

      - For grounded systems, provide a bolted line-to-ground fault-current study for areas as defined for the three-phase bolted fault short-circuit study.

    - Calculate short-circuit momentary and interrupting duties for a three-phase bolted fault and single line-to-ground fault at each of the following:

      - Electric utility's supply termination point.

      - Switchgear.

      - Unit substation primary and secondary terminals.

      - Low-voltage switchgear.

      - Motor-control centers.

      - Standby generators and automatic transfer switches.

      - Branch circuit panelboards.

    - Protective Device Evaluation:

      - Evaluate equipment and protective devices and compare to short-circuit ratings.

      - Adequacy of switchgear, motor-control centers, and panelboard bus bars to withstand short-circuit stresses.

  - ARC FLASH HAZARD ANALYSIS

    - The study shall be in accordance with latest applicable NFPA 70E, OSHA 29-CFR, Part 1910 Sub part S, IEEE 1584, and NESC Standards.  The study must be performed using IEEE 1584 for equipment rated 50 to 15 kV and NESC for equipment rated above 15 kV.

    - Use the short-circuit study output and the overcurrent protective device coordination study output or field-verified settings of the overcurrent devices.

    - Calculate maximum and minimum contributions of fault-current size.

      - The minimum calculation shall assume that the utility contribution is at a minimum and shall assume no motor load.

      - The maximum calculation shall assume a maximum contribution from the utility and shall assume motors to be operating under full-load conditions.

    - Calculate the arc-flash protection boundary and incident energy at locations in the electrical distribution system where personnel could perform work on energized parts.

    - Include medium- and low-voltage equipment locations.

    - Safe working distances shall be specified for calculated fault locations based on the calculated arc-flash boundary, considering incident energy of 1.2 cal/cm2.

    - Incident energy calculations shall consider the accumulation of energy over time when performing arc-flash calculations on buses with multiple sources. Iterative calculations shall take into account the changing current contributions, as the sources are interrupted or decremented with time. Fault contribution from motors and generators shall be decremented as follows:

      - Fault contribution from synchronous motors and generators should be decayed to match the actual decrement of each as closely as possible (e.g., contributions from permanent magnet generators will typically decay from 10 per unit to three per unit after 10 cycles).

    - Arc-flash computation shall include both line and load side of a circuit breaker as follows:

      - When the circuit breaker is in a separate enclosure.

      - When the line terminals of the circuit breaker are separate from the Work location.

    - Base arc-flash calculations on actual overcurrent protective device clearing time. Cap maximum clearing time at two seconds based on IEEE 1584, Section B.1.2.

  - LOAD-FLOW AND VOLTAGE-DROP STUDY

    - Perform a load-flow and voltage-drop study to determine the steady-state loading profile of the system. Analyze power system performance two times as follows:

      - Determine load-flow and voltage drop based on full-load currents obtained in "Power System Data" Article.

      - Determine load-flow and voltage drop based on 80 percent of the design capacity of the load buses.

      - Prepare the load-flow and voltage-drop analysis and report to show power system components that are overloaded, or might become overloaded; show bus voltages that are less than as prescribed by NFPA 70.

  - MOTOR-STARTING STUDY

    - Perform a motor-starting study to analyze the transient effect of the system's voltage profile during motor starting. Calculate significant motor-starting voltage profiles and analyze the effects of the motor starting on the power system stability. Include motors rated 50 HP and greater in study.

    - Prepare the motor-starting study report, noting light flicker for limits proposed by IEEE 141 and IEEE 519, and voltage sags so as not to affect the operation of other utilization equipment on the system supplying the motor.

  - FIELD ADJUSTMENT

    - Adjust relay and protective device settings according to the recommended settings table provided by the coordination study. Field adjustments to be completed by the engineering service division of the equipment manufacturer under the Startup and Acceptance Testing contract portion.

    - Make minor modifications to equipment as required to accomplish conformance with short-circuit and protective device coordination studies.

    - Notify Engineer in writing of any required major equipment modifications.

    - Following completion of all studies, acceptance testing and startup by the field engineering service division of the equipment manufacturer, a 2-year warranty shall be provided on all components manufactured by the engineering service parent manufacturing company.

  - ARC FLASH WARNING LABELS

    - The vendor shall provide a 3.5 in. x 5 in. thermal transfer type label of high adhesion polyester for each work location analyzed.

    - The label shall have an orange header with the wording “WARNING”, a sub-header with the wording “ARC FLASH AND SHOCK HAZARD APPROPRIATE PPE REQUIRED”, and shall include the following information:

      - Location designation

      - Nominal voltage

      - Flash protection boundary

      - Hazard risk category

      - Incident energy

      - Working distance

      - Engineering report number, revision number and issue date

      - Labels shall be machine printed, with no field markings

    - Arc flash labels shall be provided in the following manner and all labels shall be based on recommended overcurrent device settings.

      - For each 12,470, 4160, 600, 480 and applicable 208 volt panelboards and disconnects, one arc flash label shall be provided.

      - For each motor control center, one arc flash label shall be provided.

      - For each low voltage switchboard, one arc flash label shall be provided.

      - For each switchgear, one flash label shall be provided.

      - For medium voltage switches one arc flash label shall be provided.

      - For power center, one arc flash label shall be provided.

      - For control panel, one arc flash label shall be provided.

    - Labels shall be field installed by the engineering service division of the equipment manufacturer under the Startup and Acceptance Testing contract portion.

  - ARC FLASH TRAINING

    - The equipment vendor shall train personnel of the potential arc flash hazards associated with working on energized equipment (8 hours). Maintenance procedures in accordance with the requirements of NFPA 70E, Standard for Electrical Safety Requirements for Employee Workplaces, shall be provided in the equipment manuals. The training shall be certified for continuing education units (CEUs) by the International Association for Continuing Education Training (IACET).

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions