READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Medium-Voltage Metal-Clad Drawout Circuit Breaker Switchgear” Work is shown in the Contract Documents.  This section includes requirements for design, fabrication, installation and delivery of medium-voltage metal-clad drawout circuit breaker type distribution switchgear and associated auxiliary equipment.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ANSI C12.1 - American National Standard for Electric Meters - Code for Electricity Metering.

    - ANSI C37.06 - AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis - Preferred Ratings and Related Capabilities for Voltages Above 1000 V.”

    - ANSI C37.46 - Specifications for High Voltage Expulsion and Current Limiting Power Class Fuses and Fuse Disconnecting Switches

    - ANSI C39.1 - Requirements for Electrical Analog Indicating Instruments

    - ANSI/IEEE C37.04 - Structure for AC High-Voltage Circuit Breakers.

    - ANSI/IEEE C37.20.2 - Metal-Clad and Station-Type Cubicle Switchgear.

    - ANSI/IEEE C37.90 - Relays and Relay Systems Associated with Electric Power Apparatus.

    - ANSI/IEEE C57.13 - Requirements for Instrument Transformers.

    - ANSI/IEEE 48 - Test Procedures and Requirements for Alternating-Current Cable Terminations Used on Shielded Cables Having Laminated Insulation Rated 2.5 kV through 765 kV or Extruded Insulation Rated 2.5 kV through 500 kV

    - NETA ATS (InterNational Electrical Testing Association) - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems.

    - NFPA 70 - National Electrical Code as adopted and administered by the Authority Having Jurisdiction.

    - State of Washington Labor and Industries

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: For each component, including the following:

        - Features, characteristics, and ratings of individual circuit breakers.

        - Time-current characteristic curves for overcurrent protective devices, including circuit-breaker trip devices and fusible devices.

      - Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loadings, required clearances, method of field assembly, components, and location and size of each field connection. Include the following:

        - Master drawing index.

        - Front view elevation.

        - Floor plan.

        - Nameplate Schedule.

        - Nameplate diagram per ANSI requirements.

        - Single-Line Drawings.

        - Three-Line Wiring Diagrams: Detail wiring for power, signal, and control systems and differentiate between manufacturer-installed and field-installed wiring.

        - Bus configuration with size and number of conductors in each bus run, including phase, neutral, and ground conductors of main and branch buses.

        - Current ratings of buses.

        - Short-time and short-circuit ratings of switchgear assembly.

        - Conduit entry/exit locations.

        - Cable terminal sizes.

Retain paragraph below if Project involves unusual coordination requirements.

      - Coordination Drawings: Floor plans showing dimensioned layout, required working clearances, and required area above and around switchgear where pipe and ducts are prohibited. Show switchgear layout and relationships between components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate and certify field measurements.

      - Product Certificates: Signed by manufacturers of switchgear certifying that the products furnished comply with requirements.

        - Certification of compliance with seismic zone 3 rating is required.

      - Qualification Data: For firms and persons specified in “Quality Assurance” Article.

      - Field Test Reports: Indicate and interpret test results for compliance with performance requirements.

      - Product Test Reports: Indicate compliance of switchgear with requirements.

      - Operations and Maintenance Data: For switchgear to include in the maintenance manuals specified in Division 1 General Requirements.

  - QUALITY ASSURANCE

Note to Specifier: UL listed metal-clad switchgear is available with UL listing at 4.16 kV and 13.8 kV.  State of Washington Labor and Industries will require listed electrical equipment when there are two or more manufacturers that can furnish listed equipment.

    - UL Listed Equipment: Provide UL listed equipment where it is available in the specified ratings.

    - Manufacturer Qualifications: Engage a firm experienced in manufacturing switchgear similar to those indicated for this Project and with a greater than 10-year record of successful in-service performance.

    - Testing Agency Qualifications: Testing agency meeting OSHA criteria for accreditation of testing laboratories, Title 29, Part 1907 or a member company of the InterNational Electrical Testing Association and that is acceptable to Authority Having Jurisdiction.

      - Testing Agency’s Field Supervisor: Person currently certified by the InterNational Electrical Testing Association or the National Institute for Certification in Engineering Technologies to supervise on-site testing specified in Section 26 08 00 - Acceptance Testing.

    - Source Limitations: Obtain switchgear through one source from a single manufacturer.

    - Product Options: Drawings indicate size, elevations, and dimensional requirements of switchgear. Refer to Section 01 25 00 - Substitutions.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

    - Comply with ANSI/IEEE C2.

    - Comply with ANSI/IEEE C37.20.2 “Metal-Clad and Station-Type Cubicle Switchgear.”

    - Comply with ANSI/IEEE C37.04 “Structure for AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis.”

    - Comply with ANSI/IEEE C37.90 - “Relays and Relay Systems Associated with Electric Power Apparatus.”

    - Comply with ANSI C37.06 “Switchgear - AC High-Voltage Circuit Breakers Rated on a Symmetrical Current Basis - Preferred Ratings and Related Capabilities.”

    - Comply with NEMA standards.

  - DELIVERY, STORAGE, AND HANDLING

Delete paragraph below if there are no likely obstacles to handling switchgear assemblies.

    - Minimum disruption to building or systems.  Indoor splits to be bolted to skids.  Breakers and accessories to be packaged and shipped separately.

    - Deliver in shipping splits of lengths that can be moved past obstructions in delivery path as indicated. Maximum lengths should be limited to 72 inches.

    - Store so condensation will not form on or in switchgear.

    - Apply temporary heat where required to obtain suitable service conditions.

    - Handle switchgear using factory-installed lifting provisions.

    - Switchgear to be equipped for handling by crane.

    - Switchgear being stored prior to installation to be stored in a fashion to maintain equipment in a clean and dry condition

  - PROJECT CONDITIONS

Delete paragraph below if no existing utilities.

    - Existing Utilities: Do not interrupt utilities serving facilities occupied by Port or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

Edit subparagraph below to suit Project.

      - Notify the Engineer not less than seven days in advance of proposed utility interruptions.

      - Do not proceed with utility interruptions without the Engineer’s written permission.

      - Coordinate with requirements specified in Section 01 50 00 - Temporary Facilities and Controls for temporary utilities.

  - COORDINATION

    - Coordinate layout and installation of switchgear with other construction.

Delete paragraphs below if not required.

    - Coordinate size and location of concrete or mounting bases. Concrete, reinforcement, and formwork requirements are specified in Section 03 30 00 - Cast-in-Place Concrete.

    - Coordinate installation of roof curbs, equipment supports, and roof penetrations. These items are specified in Section 07 60 00 - Flashing and Sheet Metal.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided.  Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Spare Fuses: [3] of each type and rating of fuse used. Include spares for potential transformer fuses and control power fuses.

Breaker Truck: [1] breaker truck for each breaker for each line-up for removal of breakers.

Spare Breaker Carriage: [1] for each breaker type employed in a line-up.

Spare Indicating Lights: [6] of each type installed.

Touchup Paint: [3] containers of paint matching enclosure finish, each 0.5 pint.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Acceptable Manufacturers: Subject to compliance with requirements, provide products by one of the following:

F&I specifies EATON for Metal Enclosed Interrupter Switchgear, No Equal for projects at the Airport. Competition waiver to be submitted to CPO for EATON to be the only approved product for STIA, or existing waiver verified. Seaport projects may use the list of manufacturers listed below

      - Metal-Clad Circuit-Breaker Switchgear:

        - ASEA Brown Boveri, Inc.

        - EATON

        - Cutler-Hammer.

        - GE Electrical Distribution & Control.

        - Square D Co.

        - Or Approved Equal.

  - MANUFACTURED UNITS

    - Description: Factory assembled and tested, and complying with IEEE C37.20.1.

Retain paragraph below if installation space for switchgear is severely limited; show maximum dimensions on Drawings.  Ensure equipment is available.

    - Product Selection for Restricted Space: Comply with maximum dimensions indicated on Drawings. Working Space:  Provide at least 5 feet working space in front of switchgear (switchgear door width is generally at least 36”).

      - Metal-Enclosed Switchgear:  Back access to switchgear may be accomplished via suitably installed removable insulated panels in switchgear room walls unless cinder block or concrete construction is used.

      - Metal-Clad Switchgear:  Code required physical space shall be provided, NO EXCEPTIONS.

Edit to clarify applicability of conditions

    - Unusual Service Conditions: Where indicated, provide switchgear assemblies designed for the following conditions:

      - Equipment shall be rated for seismic zone 3.

  - RATINGS

Modify paragraph below to suit actual system type in which switchgear will be installed.

    - System Configuration:  Switchgear designed and suitable for operation on a 12.47 kV OR 4.16 kV, 3-phase, 3-wire, solidly grounded neutral, 60-Hz system.

Select one of five subparagraphs below or, if actual voltage is different, delete all and specify actual nominal voltage.

      - System Voltage:  12.47 kV nominal; 15 kV maximum

      - System Voltage: 4.16 kV nominal; 5 kV maximum

      - System Voltage: 4.16 kV nominal; 4.76 kV maximum.

      - System Voltage: 7.2 kV nominal; 15 kV maximum.

      - System Voltage: 13.8 kV nominal; 15 kV maximum.

    - Interrupting Rating:  AIC rating shall comply with fault current available at supply side of switchgear, including motor contribution.

    - BIL Rating

Select one of two paragraphs below

      - 60 kV BIL at 4.16 kV or 7.2 kV system voltage

      - 90 kV BIL at 12.47 kV system voltage.

  - METAL-CLAD CIRCUIT-BREAKER SWITCHGEAR

    - Vacuum switchgear designed and suitable for operation on a 12.47 kV OR 4.16 kV, 3-phase, 3-wire, reactance grounded neutral, 60-Hz system.  Switchgear main buses “A” and “B” shall be minimum 2000 amperes with 2000-ampere frame main breakers (N.C.) and tie breaker (N.O.).  Main breakers shall not be located at the end of bus.  Fault duties noted below.

    - Each circuit breaker to have the following ratings:

    - Maximum Voltage – 15 kV OR 5 kV

    - BIL Rated – 95 kV OR 60 kV

    - Short-Circuit Current at Rated Maximum kV – 18, 28, 37 kA RMS

    - Closing and Latching Capability – 62, 97, 130 kA Crest

    - Three Second Rating – 23,  36, 48 kA

    - Comply with ANSI/IEEE C37.20.2.

Select one of four paragraphs below.

    - Nominal 3-Phase MVA Class: – [250], [350], [500], [750], [1000]

    - Nominal Interrupting-Capacity Class: 250 MVA.

    - Nominal Interrupting-Capacity Class: 350 MVA.

    - Nominal Interrupting-Capacity Class: 500 MVA.

    - Ratings: Based on ANSI/IEEE C37.04 and ANSI C37.06.

Select one of two subparagraphs below; delete if shown on Drawings.

      - Main-Bus Continuous: 1200A.

      - Main-Bus Continuous: 2000A.

    - Vacuum Circuit Breakers: Drawout mounted units using three individual, vacuum-sealed contact modules and including the following features:

      - Circuit-Breaker Design: Operates at rated voltage to interrupt fault current within its rating within three cycles of trip initiation. For systems with X/R ratio of 17 or less, the transient voltage during interruption does not exceed twice the rated line-to-ground voltage of the system.

      - Contact-Wear Indicator: Readily accessible to field maintenance personnel.

      - Spare Auxiliary Contacts: Six minimum.

      - Circuit-Breaker Self-Cooled Ratings: Include the following:

Delete or revise three subparagraphs below to suit Project.

        - Current Rating of Main Circuit Breaker: 3200A.

        - Continuous Current Rating of Tie Circuit Breaker: 3200A.

        - Continuous Current Rating of Feeder Circuit Breaker: 1200A.

      - Operating Mechanism: Electrically charged, mechanically and electrically trip-free, stored-energy operated.

        - Closing Speed of Moving Contacts: Independent of both control and operator.

        - Design of Mechanism: Permits manual charging of mechanism and slow closing of contacts for inspection or adjustment.

Select one of two subparagraphs below.

          - Control Power: [48V] [125V] [250V] dc for closing and tripping.

          - Control Power: [120V] [230V] ac close and ac capacitor trip.

        - Circuit-Breaker Tripping Provisions: Shunt tripping available independent of overcurrent trip.

      - Each breaker to be complete with control switch and red, green and amber indicating lights to display the state of each breaker (open, closed, tripped) and an annunciator with provisions for resetting alarm.  Annunciator shall have provisions for remote annunciation.

      - Furnish at least 3 multi-ratio CTs for each feeder breaker, C-100 accuracy minimum.

    - Accessory Set: Tools and miscellaneous items required for circuit-breaker and switchgear test, inspection, maintenance, and operation. Include extension rails, lifting device, and transport or mobile lift, and all other items necessary to remove circuit breaker from housing and transport to remote location. Include a racking handle to move circuit breaker manually between connected and disconnected positions and a secondary test coupler to permit testing of circuit breaker without removal from switchgear. Include relay and meter test plugs.

Coordinate paragraph below with Drawings.

    - Low-dc-Voltage Alarm: Monitors dc, control power voltage and indicates an alarm at a location shown on Drawings when voltage falls to an adjustable value indicative of impending battery failure. Factory set at 80 percent of full-charge voltage. Low-Voltage Wiring:  Labeled at each terminal point

    - Grounding and Test Device System: Suitable for phasing out, testing, and grounding switchgear bus or feeder if device is installed in place of circuit breaker; includes the following:

      - Portable Grounding and Test Device: Interchangeable with drawout, medium-voltage circuit breakers to provide interlocked electrical access to either bus or feeder; electrically operated.

      - System control cabinet permanently mounted near switchgear.

      - Portable Remote-Control Station: For grounding and test device.

      - Control-Cabinet Coupler Cable: Adequate length to connect device inserted in any switchgear cubicle and control cabinet.

      - Remote-Control Coupler Cable: 50-foot cable length to connect control cabinet and portable remote-control station.

      - Permanent Control Power Wiring: From control cabinet to power source.

      - Protective Cover: Fabricated of heavy-duty plastic and fitted to device.

      - Approval of Grounding and Test Device System: Obtain approval of final system design by Port.

    - Circuit-Breaker Test Cabinet: Separately mounted and containing pushbuttons for circuit-breaker closing and tripping, control relay, fuses, and secondary coupler with cable approximately 9 feet long. Include a set of secondary devices for operating circuit breaker if removed from switchgear and moved near test cabinet. Include provision for storage of test and maintenance accessories in cabinet.

  - METAL-ENCLOSED NON-DRAWOUT LOAD INTERRUPTER SWITCHGEAR

    - Comply with ANSI/IEEE C37.20.3

    - Design Level of Available Source Fault Current:  Integrated short-circuit rating to be consistent with value of available fault current.

    - Ratings:  Comply with standard ratings for the maximum rated voltage specified.

      - Main Bus Continuous Rating – 1200 amperes

      - Main Bus Momentary (10-cycles) Current Rating:  40,000 asymmetrical rms amperes

      - Main Bus 2-Second Current Rating:  25,000 symmetrical rms amperes

    - Switches:

      - Rating:  1200 amperes continuous duty and load break.

      - Vertical Bus Momentary Current Rating:  25,000 asymmetrical rms amperes

      - Switch Fault-Closing Rating:  40,000 asymmetrical rms amperes

      - Switch 2-Second Current Rating:  25,000 symmetrical rms amperes

      - Switch Action:  No external arc and no significant quantities of ionized gas released into the enclosure.

      - Switch construction:  Supported by interior framework, with copper switch blades and stored-energy operating mechanism

      - Phase Barriers:  Provide full length of blades and fuses for each pole

      - Grounded metal barrier in front of every switch

      - Protective Shields:  Cover live components and terminals

      - Fuses de-energized when switch is open

      - Mechanical Interlock with compartment door

      - Permanent OPEN-CLOSED switch position indicators

      - High-Impact Viewing Window

      - Provisions for padlocking switch in open or closed position

    - Accessory Set:  Provide tools and miscellaneous items required for interrupter switchgear test, inspection, maintenance and operation.

    - Power Fuses:  Comply with NEMA SG2

      - Provide indicator integral with each fuse that shows when it has blown.

      - Positively mount fuses in position for easy removal from the front without special tools

      - Each fusible bay to include 3 fuses in use and 3 spare fuses in storage clips

      - Current-Limiting Fuses OR Expulsion Fuses

      - Provide interrupting ratings at rated system voltage as required.

    - Special Configurations:  Provide one of the following configurations:

      - 15-kV or 5-kV two-position non-load break selector switches for selection of two incoming sources where required

      - A duplex switchgear configuration consisting of two load interrupter switches with common load side bus to feed one load circuit, which shall be fused or unfused as required

      - An automatic transfer control relay system for two main load interrupter switches with common load bus

        - Switchgear assembly to consist of a dead-front metal-enclosed assembly including two load interrupter switches with motor operators and automatic transfer control relay system and auxiliary equipment

        - Transfer system shall be capable of automatically transferring the load bus circuit to the alternate power source upon failure of the preferred source and have capability of operating from remote signal from future Port power monitoring and control system.

    - Flooring:

      - Provide two-part epoxy floor sealant on concrete floors in rooms housing switchgear.

        - Prime coat shall be thinned and applied as recommended by coating manufacturer.

        - Drying time between coats shall be as recommended by manufacturer.

  - FABRICATION

Select from two paragraphs below to suit Project.

    - Indoor Enclosure: Steel with devices arranged as shown on contract drawings.

    - Outdoor Enclosure: Galvanized steel, weatherproof construction; integral structural-steel base frame with factory-applied asphaltic undercoating; and each compartment equipped with the following features: aisle of sufficient width to permit protective device withdrawal, disassembly, and servicing in the aisle

      - Following items to be supplied with an internal control power transformer (CPT)

      - Telephone and communications

      - Doors required with mechanism to defeat external padlocks

      - Structural design and anchorage adequate to resist loads imposed by 125-mph wind and seismic zone 3.

      - Space heater operating at one-half or less of rated voltage, sized to prevent condensation. Space heaters in each switchgear compartment and in the aisle Electric Space Heaters:  Required for outdoor installations.  Locate in each compartment with individual thermostats for each vertical section; minimum of one 250-watt space heater in each vertical section to prevent condensation, rated at 240-volts but operated at 120-volts.  Provide two or more sources of 120 VAC for space heaters.

      - Louvers equipped with insect/rodent screen and filter and arranged to permit air circulation while excluding exterior dust and rodents. Ventilation

Delete three subparagraphs below if weatherproof internal aisle construction is specified.

      - Hinged front door with padlocking provisions. Access doors with outside padlocking provisions; both doors to have panic hardware to permit exit from inside

      - Interior light with switch. Interior vaporproof fluorescent lights with low-temperature ballasts and switches at each entrance

      - Weatherproof duplex receptacle.

      - Common internal aisle of sufficient width to permit protective-device withdrawal, disassembly, and servicing in aisle.

      - Aisle access doors with outside padlocking provisions and interior panic latches.

      - Aisle space heaters operating at one-half or less of rated voltage, thermostatically controlled. Electric Space Heaters:  Required for outdoor installations.  Locate in each compartment with individual thermostats for each vertical section; minimum of one 250-watt space heater in each vertical section to prevent condensation, rated at 240-volts but operated at 120-volts.  Provide two or more sources of 120 VAC for space heaters.

      - Vaporproof fluorescent aisle lights with low-temperature ballasts, controlled by wall switch at each entrance.

      - Duplex receptacles, a minimum of two, located in aisle.

      - Aisle ventilation louvers equipped with insect/rodent screen and filter and arranged to permit air circulation while excluding exterior dust and rodents.

    - Finish: Manufacturer’s standard ANSI-61 gray finish over a rust-inhibiting primer on phosphatizing-treated metal surfaces, except when installed outdoors. Outdoor gear shall have 1.5 to 2.0 mil thick exterior finish spray coat of high-gloss gray enamel.

    - Construction Features:

Edit as required to suit project.

      - Configuration: [1-high] [2-high]

      - Access: [Front] [Rear] [Front and Rear]

      - Isolation: Each breaker section shall be individually compartmentalized.

      - Incoming Cable Compartment: [Required] [Not Required]

    - Fully Equipped Future Switchgear Compartments: Compartments shall be furnished fully equipped with rails, mounting brackets, supports, necessary bus connections, shutters, CTs, and related wiring and breaker controls.

    - Provisions for Expansion: Switchgear shall have provisions for expansion by having bus stubs at end and a covered plate for extension.

    - Bus Transition Unit: Arranged to suit bus and adjacent units.

    - Incoming-Line Unit: Arranged to suit incoming line.

    - Outgoing Feeder Units: As indicated.

    - Auxiliary Compartments: Arranged to house meters, relays, controls, and auxiliary equipment; isolated from medium-voltage components.

    - Key Interlocks: Arranged to affect interlocking schemes indicated.

    - Provisions for Future Key Interlocks: Mountings and hardware required for future installation of locks, where indicated.

  - COMPONENTS

Select one of two paragraphs below.

    - Main Bus: Copper, silver-plated at connection points. Aluminum bus is not allowed.

    - Ground Bus: Copper, silver-plated; minimum size 1/4 by 2 inches; full length of switchgear.

    - Bus Insulation: Covered with flame-retardant insulation.

    - Electric Space Heaters:  Required for outdoor installations.  Locate in each compartment with individual thermostats for each vertical section; minimum of one 250-watt space heater in each vertical section to prevent condensation, rated at 240-volts but operated at 120-volts.  Provide two or more sources of 120 VAC for space heaters.

    - Low-Voltage Wiring:  Labeled at each terminal point.

    - Utility Metering Section:  Constructed to suit Puget Sound Energy OR Seattle City Light - and EUSERC requirements at service points only.  Where feasible request utility company to install revenue metering on their side of the supply.

    - Customer Metering:

      - Utilize microprocessor-based multifunction digital metering system.  Include features for monitoring kV, A, kW, kVAR, kWh and other parameter as appropriate.  Where a main circuit breaker is furnished provide line-side voltmeters.

For STIA locations include the following subparagraph. F&I specifies EATON for electrical metering equipment, No Equal for projects at the Airport.  Competition waiver to be submitted to CPO for EATON electrical metering equipment to be the only approved product for STIA or existing waiver verified.

      - Manufacturer:  EATON PXM 6000 or 8000 series, No Equal.

      - Provide selective 3-phase voltage, current, kVA, kVAR and kWh metering for each breaker.

      - Provide totalized parameter values for bus “A” and bus “B” combined.

      - All metering shall have provisions for remote monitoring and control via existing EATON Power Net monitoring system 4-20 ma analog or digital signals.  Meter shall be fully functional with all PowerNet monitoring points available and usable for metering and monitoring.

      - Provide CTs for each meter

      - Provide PTs including primary and secondary fuses with disconnecting means.

    - Bus Transfer Controls:

      - Provide two out of three bus transfer controls wherein the two mains are momentarily paralleled for source transfer (make-before-break), and thereafter the designated main is tripped and held open.

      - Provide automatic bus transfer after loss of one source.  The affected main breaker shall be tripped and held open.

      - Include provisions to prevent automatic closure of the tie breaker to a faulted bus.

    - Instrument Transformers: Comply with ANSI/IEEE C57.13. Instrument Transformers:  PTs and CTs as indicated.  PTs with secondary voltage rating of 120V, Class 0.3 with burdens of W, X and Y, and multi-ratio CTs as appropriate.  Provide .5% minimum utility accuracy class CTs, as required, for metal-clad switchgear.

      - Potential Transformers: Secondary voltage rating of 120V and NEMA accuracy class of 0.3 with burdens of W, X, and Y, and multi-ratio CTs as appropriate.

Coordinate subparagraph below with Drawings.

      - Current Transformers: Ratios as indicated; burden and C-200 minimum accuracy class suitable for connected relays, meters, and instruments.

    - Multifunction Digital-Metering Monitor: UL-listed or -recognized, microprocessor-based unit suitable for three- or four-wire systems and with the following features:

      - Inputs from sensors or 5A current-transformer secondaries, and potential terminals rated to 600V.

      - Switch selectable digital display of the following:

        - Phase Currents, Each Phase: Plus or minus 1 percent.

        - Phase-to-Phase Voltages, Three-Phase: Plus or minus 1 percent.

        - Phase-to-Neutral Voltages, Three-Phase: Plus or minus 1 percent.

        - Three-Phase Real Power: Plus or minus 2 percent.

        - Three-Phase Reactive Power: Plus or minus 2 percent.

        - Power Factor: Plus or minus 2 percent.

        - Frequency: Plus or minus 0.5 percent.

        - Integrated Demand, with Demand Interval Selectable from 5 to 60 Minutes: Plus or minus 2 percent.

Delete subparagraph below if not required.

        - Accumulated energy, in megawatt hours, plus or minus 2 percent; stored values unaffected by power outages for up to 72 hours.

      - Relay shall have communication port for data and control communication. Port shall be compatible with the Port’s Power Monitoring and Control System.

      - Mounting: Display and control unit flush or semi-flush mounted in instrument compartment door.

Delete paragraph below unless relays not integral with circuit breakers or circuit-breaker trip units are required.  Specify relay functions and characteristics below or indicate on Drawings.

    - Relays: Comply with ANSI/IEEE C37.90, types and settings as indicated; with test blocks and plugs.

      - Solid-state with continuous self-diagnostics, draw-out mounted, complying with IEEE C37.90 and as indicated on the drawings

      - Provide in the metal-clad circuit breaker, metal-enclosed interrupter switchgear, the quantity, type and rating of protection relays indicated on the drawings

      - Microprocessor Three-Phase Protective Relay with ANSI 50/51, 50/51G or 50/51N incorporated into a single device, Basler BE1-851, EATON type (Westinghouse) Digitrip-3000, Or Approved Equal; relay shall have long-time, short-time, instantaneous and ground-fault settings. Provide necessary software and licenses to set all relays.

      - Relays shall have remote monitoring and metering communication capability via Ethernet compatible with Eaton PXM web server communications protocols.

      - Provide differential bus protection (minimum of two zones, ANSI device 87).

      - Provide a lockout relay (ANSI device 86) for every breaker.

      - Provide separate ANSI devices 50/51 and 50G (or 51G) for each feeder breaker with local alarm and annunciation.

      - Provide synch check relays (ANSI device 25) for main breakers and tie, and for intertie to other active sources.

      - Provide an ANSI device 51/51N for each main breaker.

Show ratings of arresters on Drawings.

    - Surge Arresters:

      - Incoming Line Main Circuit Breakers: Provide suitably rated intermediate class, metal-oxide varistor type, complying with NEMA LA-1, connected in each phase of circuit, and grounded to the metal structure, for each incoming line section.

      - Feeder Breakers: Where required provide suitably rated intermediate class, metal-oxide varistor type, complying with NEMA LA-1, connected in each phase of circuit, and grounded to the metal structure, for each feeder section.

      - Coordinate rating with circuit voltage.

    - Weatherproof Housing with Aisle (Metal-Clad Circuit Breaker Switchgear Only):  Galvanized-steel construction; integral structural steel base frame with factory-applied asphaltic undercoating; aisle of sufficient width to permit protective device withdrawal, disassembly, and servicing in the aisle

      - Access doors with outside padlocking provisions; both doors to have panic hardware to permit exit from inside

      - Following items to be supplied with an internal control power transformer (CPT)

      - Space heaters in each switchgear compartment and in the aisle

      - Ventilation

      - Telephone and communications

      - Interior vapor proof fluorescent lights with low-temperature ballasts and switches at each entrance

      - Minimum of two duplex receptacles

      - Louvers with insect/rodent screens and filters and arranged to permit air circulation

      - Wind resistance of 125 mph

      - Doors required with mechanism to defeat external padlocks

    - Provide overhead hoist and cart for servicing switchgear

    - Identification Nameplates:

    - Conform to Port Standard Nameplate labeling in Section 26 05 53 – Electrical Identification;

      - Engraved nameplates to be mounted on the face of the enclosure for all main and feeder circuits

      - Nameplates to be laminated plastic, black characters on white background, and secured with stainless steel screws

      - Nameplates to identify source of feed and loads served, and include applicable warnings

      - All control components mounted within the assembly to be suitably marked for identification corresponding to manufacturer’s wiring diagrams.

    - Finish:  The finish shall consist of manufacturer’s standard ANSI-61 gray finish, except when installed outdoors.  Outdoor gear to have 3.0 mil thick exterior finish spray coat of high-gloss gray enamel.

    - Fully Equipped Future Switchgear Spaces:  Spaces shall be furnished fully equipped with bus bars, shutters, CTs, and related wiring and breaker controls.

    - Provisions for Expansion:  Switchgear shall have provisions for expansion by having bus stubs at end and a covered plate for extension.

    - Conduit Access:  Provide knockouts for a minimum of two 6-inch conduits top and bottom.

    - Spare Conduits:  Provide a minimum of one 6-inch conduit per bus section.

    - Control Power Supply: DC battery system.

Select paragraph above or below. If retaining above, retain “Control Battery System” Article below.

    - Control Power Supply: Control power transformer supplies 120V control circuits through secondary disconnect devices. Include the following features:

      - Dry-type transformers, in separate compartments for units larger than 3 kVA, including primary and secondary fuses.

Retain subparagraph below for electrically interlocked main and tie circuit breakers.

      - Two control power transformers in separate compartments with necessary interlocking relays; each transformer connected to line side of associated main circuit breaker.

Delete one of two subparagraphs below.

        - Secondaries connected through a relay or relays to control bus to affect an automatic transfer scheme.

        - Secondaries connected through an internal automatic transfer switch to switchgear control power bus.

      - Control Power Fuses: Primary and secondary fuses provide current-limiting and overload protection.

    - Control Wiring: Factory installed, complete with bundling, lacing, and protection, and complying with the following:

      - Flexible conductors for #8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

      - Conductors sized according to NFPA 70 for the duty required.

  - CONTROL BATTERY SYSTEM

Revise if battery other than lead-calcium type below is specified.  Coordinate paragraph below with Drawings or, preferably, revise to specify number of cells and required minimum ampere-hour capacity of battery.

    - System Requirements: Battery has number of cells and ampere-hour capacity and rating as indicated, based on an initial specific gravity of 1.210 at 25°C with electrolyte at normal level and minimum ambient temperature of 13°C. Cycle battery before shipment to guarantee rated capacity on installation. Arrange battery to operate ungrounded.

    - Battery: [Lead-calcium] OR [Gel Cell] type in sealed, clear plastic or glass containers, complete with electrolyte, fully charged, and arranged for shipment with electrolyte in cells. Each container weighs not more than 70 lb and contains not more than three cells. Batteries are suitable for service at an ambient temperature ranging from minus 18 to 25°C. Current output does not vary more than 0.8 percent for each degree below 25°C down to minus 8°C.

Coordinate two paragraphs below with Drawings.

    - Rack: Provide a two-step rack that fits available space indicated. Seismic zone batteries are provided with necessary electrical connections between cells and between rows of cells and include two flexible connectors with bolted-type terminals for output leads.

    - Accessories: Include the following:

      - One DC circuit breaker shall supply power to no more than one switchgear section.

      - Switchgear main breakers shall have line-side and bus-side PTs (Star-star connection shall not be acceptable).

      - Dry-type CPTs at the line side of each source supply to switchgear. Secondary of CPTs shall be 240/120V, single-phase. Minimum rating of each CPT shall be 10 kVA.

      - Properly rated 120/240V rated automatic transfer switch to feed station battery charger and station lighting load during loss of power.

      - Thermometers with specific-gravity correction scales.

      - Hydrometer syringes.

      - Set of socket wrenches and other tools required for battery maintenance.

      - Wall-mounted, nonmetallic storage rack fitted to store above items.

      - Set of cell numerals.

    - Charger: Static-type silicon rectifier equipped with automatic regulation and provision for manual and automatic adjustment of the charging rate. Unit automatically maintains output voltage within 0.5 percent from no load to rated charger output current, with ac input-voltage variation of plus or minus 10 percent and input-frequency variation of plus or minus 3 Hz. Other features of charger include the following:

      - DC ammeter.

      - DC Voltmeter: Maximum error of 5 percent at full-charge voltage; operates with toggle switch to select between battery and charger voltages.

      - Ground Indication: Two appropriately labeled lights to indicate circuit ground, connected in series between negative and positive terminals, with midpoint junction connected to ground by normally open push-button contact.

      - Capacity: Sufficient to supply steady load, float-charge battery between 2.20 and 2.25V per cell, and equalizing charge at 2.33V per cell.

      - Charging-Rate Switch: Manually operated switch provides for transferring to higher charging rate. Charger operates automatically after switch operation until manually reset.

      - AC power supply is 120V, 60Hz, subject to plus or minus 10 percent variation in voltage and plus or minus 3 Hz variation in frequency. After loss of ac power supply for any interval, charger automatically resumes charging battery. Charger regulates rate of charge to prevent damage due to overload and to prevent fuses or circuit breakers from opening.

      - Protective Feature: Current-limiting device or circuit, which limits output current to rating of charger but does not disconnect charger from either battery or ac supply; to protect charger from damage due to overload, including short circuit on output terminals.

      - Electrical Filtering: Reduces charger’s audible noise to less than 26 dB.

- EXECUTION

  - INSTALLATION

    - Locations and Layout: Exact locations and physical layout of equipment and components may be varied as required to suit manufacturer’s design and as approved, provided the required functions and operations are accomplished; follow the identification of the units indicated on Drawings exactly.

    - Vaults shall be provided beneath medium-voltage switchgear lineups to facilitate termination of cables.

    - Anchor each switchgear assembly to at least two 4-inch, channel-iron floor sills arranged in accordance with manufacturer’s written recommendations and seismic zone 3 requirements. Attach by tack welding or bolting.

      - Retain a Professional Structural Engineer who is licensed in the State of Washington and who is experienced in providing seismic engineering services to provide seismic calculations for each switchgear assembly. Comply with Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

      - Sills: Select to suit switchgear; level and grout flush into floor or concrete or mounting base.

      - Concrete Bases: 4 inches high, reinforced, with chamfered edges. Extend base no more than 2 inches in all directions beyond the maximum dimensions of the switchgear, unless otherwise indicated. Comply with Section 03 30 00 - Cast-in-Place Concrete.

    - Temporary Lifting Provisions: Remove temporary lifting eyes, channels, brackets, and temporary blocking of moving parts from switchgear units and components.

  - CONNECTIONS

    - Connect switchgear ground bus to common building ground or, for outdoor switchgear, ground switchgear ground bus to ground grid.

    - Refer to Section 26 05 13 - Medium-Voltage Cables for types of medium-voltage cable terminations.

    - Tighten bus joint, connector, and terminal bolts according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A and UL 486B.

      - Mark lugs after torquing with red paint such that paint will be visibly disturbed if lugs are disturbed.

  - IDENTIFICATION

    - Identify field-installed wiring and components and provide warning signs as specified in Section 26 05 53 - Electrical Identification.

    - Identify equipment name, designation, power source, source location and voltage rating.

    - Identify all devices, controls, and wiring.

    - Provide warning and caution signs where indicated or required by the Authority Having Jurisdiction.

    - Equipment used in emergency systems shall be labeled “Suitable for use on emergency systems” per NEC 700-3.

    - Diagram and Instructions: Frame under clear acrylic plastic on the front of switchgear.

      - Operating Instructions: Printed basic instructions for switchgear, including control and key-interlock sequences and emergency procedures.

      - Storage for Manual: Include a rack or holder, near the operating instructions, for a copy of the maintenance manual.

      - System Power Riser Diagrams: Depict power sources, feeders, distribution components, and major loads.

Delete paragraph below if not required.

    - Mimic Bus: Continuous mimic bus applied to front of switchgear, arranged in single-line diagram format, using symbols and lettered designations consistent with approved final mimic-bus diagram.

      - Mimic-bus segments coordinated with devices in switchgear sections to which applied, to produce a concise visual presentation of principal switchgear components and connections.

      - Medium: Painted graphics.

      - Color: Contrasting with factory-finish background, selected by the Engineer.

  - FIELD QUALITY CONTROL

Retain paragraph below unless qualified services are available outside manufacturer’s service group.

    - Manufacturer’s Field Services: Engage a factory-authorized service representative to assist in installation and start-up of the equipment. The manufacturer’s representative shall provide technical direction and assistance to the Contractor in general assembly of the equipment, connections and adjustments, and testing of the assembly and components contained therein.

    - Testing Agency: Engage a qualified independent testing firm to perform field quality-control testing as specified in Section 26 08 00 - Acceptance Testing.

      - Electrical Contractor shall accompany the independent testing firm field service technician and assist as required during field tests.

  - ADJUSTING

    - Protective-Relay Settings:

      - Provide a protective relay coordination study by an Electrical Engineer licensed in the State of Washington.

      - Verify that settings shown on Drawings are appropriate for final system configuration and parameters. Where discrepancies are found, recommend final relay settings for approval before making final adjustments.

Select one of the following two subparagraphs:

      - The relays shall be set in the field by the Contractor in accordance with settings shown in a coordination study by the Engineer.

      - The relays shall be set in the field by a qualified representative of the manufacturer, retained by the Contractor, in accordance with settings designated in a coordinated study required elsewhere in the specifications.

    - Fuse Characteristics: Verify that fuse size and types shown on Drawings are appropriate for final system configuration and parameters. Where discrepancies are found, recommend fuse selection for approval before making final adjustments.

  - CLEANING

    - Inspect interior and exterior of installed switchgear. Remove paint splatters and other spots, dirt, and debris. Touch up scratches and mars of finish to match original finish.

  - PROTECTION

    - Temporary Heating: Apply temporary heat to switchgear, according to manufacturer’s written recommendations, throughout periods when switchgear environment is not controlled for temperature and humidity within manufacturer’s stipulated service conditions.

  - DEMONSTRATION AND TRAINING

    - Engage a factory-authorized service representative to train Port’s maintenance personnel in the following:

      - Train Port’s maintenance personnel on procedures and schedules related to startup and shutdown, troubleshooting, servicing, and preventive maintenance for two normal workdays at the jobsite.

      - Review data in the maintenance manuals. Refer to Section 01 78 23.13 - Operations and Maintenance Data.

      - Schedule training with Port with at least seven days’ advance notice.

  - OPERATION AND MAINTENANCE MANUALS

    - Comply with Section 01 78 23.13 - Operations and Maintenance Data and Part 1 of this specification.

    - Gather record drawings and as-furnished information for switchgear (including appurtenances, battery charger, PTs, relays, etc.) and generate an “integrated, unit specific, operation and maintenance manual”, complete with schematic diagrams of upstream/downstream systems feeding and being fed by “this” system.

      - Location of devices, PTs, CTs, relays, metering for “this” switchgear shall be clearly identified and the function of each unit in the overall scheme of things explained.

      - A binder containing a collection of generic switchgear device cut sheets and disjointed O&M guidelines for generic switchgear does not meet this requirement.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Sole Source