READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Motor-Control Centers” Work is shown in the Contract Documents. This section includes motor-control centers for use on AC circuits rated 600V and less.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - IEEE C62.41 (Institute of Electrical and Electronics Engineers) - Recommended Practice on Surge Voltages in Low-Voltage AC Power Circuits.

    - NEMA AB 1 (National Electrical Manufacturers Association) - Molded Case Circuit Breakers.

    - NEMA FU 1 (National Electrical Manufacturers Association) – Low Voltage Cartridge Fuses.

    - NEMA ICS 2 (National Electrical Manufacturers Association) - Industrial Control and Systems: Controllers, Contactors, and Overload Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC.

    - NEMA ICS 2.3 (National Electrical Manufacturers Association) - Instructions for the Handling, Installation, Operation, and Maintenance of Motor Control Centers Rated Not More Than 600V.

    - NEMA ICS 3 (National Electrical Manufacturers Association) - Industrial Control and Systems: Factory Built Assemblies.

    - NEMA ICS 5 (National Electrical Manufacturers Association) - Industrial Control and Systems: Control Circuit and Pilot Devices.

    - NEMA KS 1 (National Electrical Manufacturers Association) - Enclosed and Miscellaneous Distribution Equipment Switches (600 Volts Maximum).

    - NETA ATS (International Electrical Testing Association) - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems.

    - NFPA 70 (National Fire Protection Association) - National Electrical Code.

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: For each type of controller and each type of motor-control center. Include dimensions and manufacturer’s technical data on features, performance, electrical characteristics, ratings, and finishes.

      - Shop Drawings: For each motor-control center.

        - Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment. Show tabulations of installed devices, equipment features, and ratings. Include the following:

          - Each installed unit’s type and details.

          - Factory-installed devices.

          - Enclosure types and details.

          - Nameplate legends.

          - Short-circuit current ratings of buses and installed units.

          - Vertical and horizontal bus capacities.

          - UL listing for series rating of overcurrent protective devices in combination controllers.

          - Features, characteristics, ratings, and factory settings of each motor-control center unit.

        - Wiring Diagrams: Power, signal, and control wiring for class and type of motor-control center. Differentiate between manufacturer-installed and field-installed wiring. Provide schematic wiring diagram for each type of controller.

      - Manufacturer Seismic Qualification Certification: Submit certification that motor-control centers, accessories, and components will withstand seismic forces defined in Section 26 05 48 - Seismic Controls for Electrical and Communication Work. Include the following:

        - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - The term “withstand” means “the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event.”

      - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

      - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

      - Field Test Reports: Written reports specified in Part 3.

      - Manufacturer’s field service report.

      - Maintenance Data: For motor-control centers, all installed devices, and components to include in maintenance manuals specified in Division 1 General Requirements. In addition to requirements specified in Section 01 78 23.13 - Operations and Maintenance Data include the following:

        - Routine maintenance requirements for motor-control centers and all installed components.

        - Manufacturer’s written instructions for testing and adjusting overcurrent protective devices.

Select one of the two following paragraphs below to suit type of motor running overload protection specified in Part 2.

      - Load-Current and Overload-Relay Heater List: Compile after motors have been installed and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents.

      - Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed and arrange to demonstrate that dip switch settings for motor running overload protection suit actual motor to be protected.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Maintain, within 100 miles of Project site, a service center capable of providing training, parts, and emergency maintenance and repairs.

    - Source Limitations: Obtain controllers of a single type through one source from a single manufacturer.

    - Listing and Labeling: Provide electrical components, devices and accessories that are Listed and Labeled as defined in NFPA 70, Article 100 and marked for intended use for the location and environment in which they are installed.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

Motor-control centers with the same functional characteristics may vary slightly in length and depth among manufacturers. If installation space is severely limited, show maximum dimensions on Drawings, ensure that equipment is available to fit, and retain below. Delete below if space is not a concern.

    - Product Selection for Restricted Space: Drawings indicate maximum dimensions for motor-control centers, including clearances between motor-control centers, and for adjacent surfaces and other items. Comply with indicated maximum dimensions.

  - DELIVERY, STORAGE, AND HANDLING

Revise this Article to refer to other Divisions, such as Division 14 Conveying Equipment for baggage conveyor systems, if control coordination is required.

Delete first paragraph below if no obstacles to movement of normal shipping lengths of motor-control centers. Coordinate with Drawings.

    - Deliver motor-control centers in shipping splits of lengths that can be moved past obstructions in delivery path as indicated.

    - Handle motor-control centers according to NEMA ICS 2.3, “Instructions for the Handling, Installation, Operation, and Maintenance of Motor Control Centers.” and NECA 402, "Recommended Practice for Installing and Maintaining Motor Control Centers." Use factory-installed lifting provisions.

    - Store motor-control centers indoors in clean, dry space with uniform temperature to prevent condensation. Protect motor-control centers from exposure to dirt, fumes, water, corrosive substances, and physical damage.

      - If stored in areas subjected to weather, cover motor-control centers to protect from weather, dirt, dust, corrosive substances, and physical damage. Remove loose packing and flammable materials from inside controllers; install electric heating of sufficient wattage to prevent condensation.

  - COORDINATION

No piping or ducts are allowed over MCCs.

    - Coordinate layout and installation of motor-control centers with other construction including conduit, piping, equipment, and adjacent surfaces. Maintain required workspace clearances and required clearances for equipment access doors and panels, and for ventilation.

    - Coordinate size and location of concrete bases. Refer to Section 03 30 00 - Cast-in-Place Concrete for concrete, reinforcement, and formwork requirements.

    - Coordinate features of motor-control centers, installed units, and accessory devices with pilot devices and control circuits to which they connect.

    - Coordinate features, accessories, and functions of each motor-control center, each controller, and each installed unit with ratings and characteristics of supply circuit, motor, required control sequence, and duty cycle of motor and load.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided.  Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Spare Fuses: [3] of each type and rating installed.

Indicating Lights: [2] of each type installed.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Allen-Bradley.

      - Cutler-Hammer; Division of Eaton.

      - General Electric.

      - Square D.

      - Or Approved Equal.

  - MOTOR-CONTROL CENTERS

    - Wiring: NEMA ICS 3, Class II, Type B.

    - UL Listed: Service Entrance Label where used as a service entrance.

    - Enclosures: 600-volt, dead-front, front access, free standing units manufactured to withstand seismic forces as described in Section 26 05 48 – Seismic Controls for Electrical and Communication Work.

Front access is standard and preferred.  Front and rear mounted starter units and circuit breakers acceptable if warranted by design constraints.

No cabling shall be allowed for any interconnections of MCC sections unless approved by Facilities and Infrastructure.

      - Provide side gutters for ease of wiring.

      - Indoor Clean, Dry Locations: NEMA 250, Type 1A, gasketed.

      - Indoor Locations Subject to Wet or Dry Contaminants: NEMA 250, Type 12.

      - Outdoor Locations: NEMA 250, Type 3R.

        - Include space heater for prevention of condensation.

    - Compartments: Modular, with individual 120° swing doors, concealed hinges and quick-captive screw fasteners.

      - Include interlocks on combination controller units requiring disconnecting means in off position before door can be opened or closed, except by operating a permissive release device.

      - Include bus-isolating mechanism on draw-out units.

    - Interchangeability: Compartments constructed to allow for removal of units without opening adjacent doors, disconnecting adjacent compartments, or disturbing operation of other units in motor-control center. Interchangeability of units requiring the same size compartment and constructed to permit ready rearrangement of units, such as replacing three single units with a unit requiring three spaces, without cutting or welding.

    - Wiring Spaces: Wiring channel in each vertical section for vertical and horizontal wiring to each unit compartment, with supports to hold wiring in place.

Coordinate below with Drawings.

    - Short-Circuit Current Rating for Each Section: Equal to or greater than indicated available fault current in symmetrical amperes at motor-control center location.

  - BUSES

Note: Aluminum bus is not allowed.  Bus withstand rating with 65 kA rms.

    - Horizontal Bus.

      - Material: Tin-plated copper.

      - Ampacity Ratings: 600 amperes minimum.

    - Vertical Bus.

      - Material: Tin-plated copper.

      - Ampacity Ratings: 300 amperes minimum.

    - Neutral Buses: Full size. Hard-drawn copper of 98 percent conductivity, tin plated.

    - Equipment Ground Bus: Noninsulated, horizontal copper bus, 98 percent conductivity, 1-inch by 1/4-inch minimum.

    - Horizontal Bus Arrangement: Main phase, neutral and ground buses extended with same capacity the entire length of motor-control center, with provision for future extension at both ends by bolt holes and captive bus splice sections or equivalent.

Coordinate below with Drawings.

    - Short-Circuit Withstand Rating: Same as short-circuit current rating of section.

  - FUNCTIONAL FEATURES

    - Description: Modular arrangement of main units, controller units, control devices, feeder-tap units, instruments, metering, auxiliary devices, and other items mounted in vertical sections of MCC.

    - Required Features

      - Main circuit breaker is required when MCC is located where user group does not have access to MCC feeder circuit breaker.

      - Main circuit breaker shall be equipped with electronic trip or electronic programmable trip.

      - Monitoring of main overcurrent protective device is required except when the feeder to the MCC is monitored.  See “Circuit Breaker Trip and Monitoring Requirements” schedule in appendix to Design Principles.

      - Lockout means accommodating up to three padlocks for main circuit breaker and each individual load fed by MCC.

      - Provide neutral bus and neutral conductor for all MCCs.

      - Equipment shall be rated for available fault current.  Give consideration to future increases in available fault currents when determining fault ratings.

    - Controller Units: Combination controller units of types and with features, ratings, and circuit assignments indicated.

      - Install units with full-voltage, across-the-line, magnetic controllers up to and including Size 5 on drawout mountings with connectors that automatically line up and connect with vertical-section buses while being racked into their normal, energized positions.

        - Motor Circuit Protector (MCP or HMCP) unless available fault current exceeds 65,000 Amps symmetrical. This device provides controller and motor disconnect means and overcurrent protection. Adjustable magnetic settings up to 1300% of motor FLA.

        - Fused switches are allowed where available fault current exceeds 65,000 amps symmetrical, or for coordination reasons.

        - Two normally open and two normally closed reversible auxiliary contacts minimum.

      - Provide units with short-circuit current ratings equal to or greater than short-circuit current rating of motor-control center section.

      - Equip units in Type B and Type C motor-control centers with pull-apart terminal strips or drawout terminal boards for external control connections.

    - Overcurrent Protective Devices: Individual feeder-tap units through 225A rating shall have drawout mountings with connectors that automatically line up and connect with vertical-section buses while being racked into their normal, energized positions.

Coordinate two paragraphs below with Drawings. Indicate, in schedule, sizes of future controllers to be accommodated.

    - Spaces and Blank Units: Compartments fully bused and equipped with guide rails or equivalent, ready for insertion of drawout units.

    - Spare Units: Type, sizes, and ratings indicated; installed in compartments indicated “spare.”

  - MAGNETIC MOTOR CONTROLLERS

    - Starting methods may include, but are not limited, to the following:

      - Full Voltage Non-reversing

      - Full Voltage Reversing

      - Two-Speed One-Winding

      - Two-Speed Two-Winding

      - Reduced-Voltage Autotransformer

      - Reduced-Voltage Part-Winding

      - Reduced-Voltage Wye Delta open or closed transition

      - Variable frequency drives  (refer to Section 26 29 23 – Variable Frequency Controllers)

      - Solid-state reduced-voltage

      - Solid-state reduced-voltage with contactor bypass

      - Solid-state soft-start

    - Description: NEMA ICS 2, ClassA, full voltage, nonreversing, across-the-line, unless otherwise indicated.

Select one of two paragraphs below. Coordinate paragraph above and two paragraphs below with Drawings.

    - Control Circuit: 120V obtained from integral control power transformer, one size larger than required to operate connected pilot, indicating and control devices. Include primary and secondary overcurrent protection.  The secondary of the CPT shall have one leg grounded. No switching of coils shall be allowed between the coil and the groundside.

    - Control Circuit: 120V external power source. Include auxiliary contacts, mechanically tied to the combination starter disconnect switch and wired so that control power within the motor starter module will be disconnected when the motor power disconnect is opened.  The secondary of the CPT shall have one leg grounded. No switching of coils shall be allowed between the coil and the groundside.

    - Combination Controller: Factory-assembled combination controller and disconnect switch.

Use subparagraph 2 below involving fused disconnect only if available fault current exceeds 65kAIC.

      - Combination Draw-out Starter Units (size 1 through size 5):  These units are standard for all suitable applications and shall include:

        - MCP Disconnecting Means:

          - Use where available fault current is 65,000 Amps symmetrical or less.

          - UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable up to 1300% of motor FLA, short-circuit trip coordinated with motor locked-rotor amperes.

          - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Fused Disconnecting Means

          - Use where available fault current exceeds 65,000 Amps symmetrical or for coordination reasons.

          - NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate indicated fuses.

          - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Two normally open and two normally closed reversible auxiliary contacts minimum.

        - Motor controller preferred features include:

          - Current sensor / microprocessor type overload protection with adjustable parameters including overcurrent, ground fault, phase loss, phase unbalance, undervoltage, overvoltage.

          - Silver-plated contacts.

        - 120-Volt control power transformer (CPT) in each starter module with primary and secondary overcurrent protection.  Size CPT at least one size above minimum VA requirements.  Should an external control power source be required, provide auxiliary contacts mechanically tied to the combination starter disconnect switch and wired so that control power within the motor starter module will be disconnected when the motor power disconnect is opened.  The secondary of the CPT shall have one leg grounded no switching of coils shall be allowed between the coil and the groundside.

        - Control pushbuttons mounted on front of MCC modules shall be industrial oil-tight type.

        - Standard control for remotely controlled motors is hand-off-auto (HOA) mounted in front panel of each module.

        - Standard push-to-test pilot lights shall be red “running” and green “ready” mounted in front panel of individual modules.

        - Pilot lights:  Preferred type is oil-tight transformer LED type.

F&I specifies EATON for electrical metering equipment, No Equal for projects at the Airport. Competition waiver to be submitted to CPO for EATON electrical metering equipment to be the only approved product for the STIA, or existing waiver verified, and include following subparagraph.

        - Metering:  Make provisions for remote monitoring and revenue metering.  Meters shall be EATON, No Equal, PXM 2000 series with Modbux TCP/IP Ethernet based monitoring system.

Select one of two paragraphs below

    - Overload Relay: Ambient-compensated type with inverse-time-current characteristic and NEMA ICS 2, Class [10] [20] [30] tripping characteristic. Provide with heaters or sensors in each phase matched to nameplate full-load current of specific motor to which they connect and with appropriate adjustment for duty cycle.

    - Adjustable Overload Relay: Dip switch selectable for motor running overload protection with NEMA ICS 2, Class [10] [20] [30] tripping characteristic, and selected to protect motor against overvoltage, undervoltage, overcurrent, phase unbalance and phase loss. Provide relay with Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

Coordinate paragraph and subparagraphs below with Drawings.

    - Reduced-Voltage Magnetic Controllers:

      - General Requirements for Reduced-Voltage Magnetic Controllers: Comply with NEMA ICS 2, general purpose, Class A; closed transition; adjustable time delay on transition.

      - Reduced-Voltage Magnetic Controllers: Reduced voltage, electrically held.

        - Wye-Delta Controller: Four contactors, with a three-phase starting resistor/reactor bank. Open or closed transition.

        - Part-Winding Controller: Separate START and RUN contactors, field-selectable for one-half or two-thirds winding start mode, with either six- or nine-lead motors; with separate overload relays for starting and running sequences.

        - Autotransformer Reduced-Voltage Controller: Medium-duty service, with integral overtemperature protection; taps for starting at 50, 65, and 80 percent of line voltage; two START and one RUN contactors.

    - Reduced-Voltage, Solid-State Controllers:

      - General Requirements for Reduced-Voltage, Solid-State Controllers: Comply with UL 508.

      - Reduced-Voltage, Solid-State Controllers: An integrated unit with power SCRs, heat sink, microprocessor logic board, door-mounted digital display and keypad, bypass contactor, and overload relay; suitable for use with NEMA MG 1, Design B, polyphase, medium-induction motors.

        - Configuration: Severe duty, reversible OR nonreversible.

        - Starting Mode: Voltage ramping OR Current limit OR Torque control OR Torque control with voltage boost OR; field selectable.

        - Stopping Mode: Coast to stop OR Adjustable torque deceleration OR Adjustable braking OR field selectable.

        - Shorting (Bypass) Contactor: Operates automatically when full voltage is applied to motor, and bypasses the power semiconductors. Solid-state controller protective features shall remain active when the shorting contactor is in the bypass mode.

        - Shorting and Input Isolation Contactor Coils, if needed: Pressure-encapsulated type; manufacturer's standard operating voltage, matching control power or line voltage, depending on contactor size and line-voltage rating. Provide coil transient suppressors.

        - Logic Board: Identical for all ampere ratings and voltage classes, with environmental protective coating.

        - Adjustable acceleration-rate control using voltage or current ramp, and adjustable starting torque control with up to 400 percent current limitation for 20 seconds.

        - Keypad, front accessible; for programming the controller parameters, functions, and features; shall be manufacturer's standard and include not less than the following functions:

          - Adjusting motor full-load amperes, as a percentage of the controller's rating.

          - Adjusting current limitation on starting, as a percentage of the motor full-load current rating.

          - Adjusting linear acceleration and deceleration ramps, in seconds.

          - Initial torque, as a percentage of the nominal motor torque.

          - Adjusting torque limit, as a percentage of the nominal motor torque.

          - Adjusting maximum start time, in seconds.

          - Adjusting voltage boost, as a percentage of the nominal supply voltage.

          - Selecting stopping mode, and adjusting parameters.

          - Selecting motor thermal-overload protection class between 5 and 30.

          - Activating and de-activating protection modes.

        - Digital display, front accessible; for showing motor, controller, and fault status; shall be manufacturer's standard and include not less than the following:

          - Controller Condition: Ready, starting, running, stopping.

          - Motor Condition: Amperes, voltage, power factor, power, and thermal state.

          - Fault Conditions: Controller thermal fault, motor overload alarm and trip, motor underload, overcurrent, shorted power semiconductors, line or phase loss, phase reversal, and line frequency over or under normal.

        - Controller Diagnostics and Protection:

          - Microprocessor-based thermal protection system for monitoring power semiconductor and motor thermal characteristics, and providing controller overtemperature and motor overload alarm and trip; settings selectable via the keypad.

          - Protection from line-side reverse phasing; line-side and motor-side phase loss; motor jam, stall, and underload conditions; and line frequency over or under normal.

        - For controllers without integral disconnects, provide input isolation contactor that opens when the controller diagnostics detect a faulted solid-state component, or when the motor is stopped.

        - For combination motor starter/disconnect, provide shunt trip that opens the disconnecting means when the controller diagnostics detect a faulted solid-state component.

        - Remote Output Features:

          - All outputs prewired to terminal blocks.

          - Form C status contacts that change state when controller is running.

          - Form C alarm contacts that change state when a fault condition occurs.

        - Analog output for field-selectable assignment of motor operating characteristics; 4 to 20-mA dc.

        - Additional field-assignable Form C contacts for alarm outputs.

        - Surge suppressors in solid-state power circuits providing three-phase protection against damage from supply voltage surges 10 percent or more above nominal line voltage.

    - Multispeed Magnetic Controllers:

      - General Requirements for Multispeed Magnetic Controllers: Comply with NEMA ICS 2, general purpose, Class A.

      - Multispeed Magnetic Controllers: Two speed, full voltage, across the line, electrically held. Compelling relay to ensure that motor will start only at low speed.

        - Configuration: One or two winding, reversing or Nonreversing, depending on application.

        - Compelling relays shall ensure that motor starts only at low speed.

        - Accelerating timer relays shall ensure properly timed acceleration through speeds lower than that selected.

        - Decelerating timer relays shall ensure automatically timed deceleration through each speed.

    - Auxiliary Contacts: Include two normally-open and two normally-closed auxiliary contacts minimum for each controller.

  - VARIABLE-FREQUENCY CONTROLLERS

    - Refer to Section 26 29 23 - Variable Frequency Controllers.

  - OVERCURRENT PROTECTION

Edit this Article to suit Project. Coordinate with Drawings.

    - Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250A and larger. Lockout means accommodating up to three padlocks.

      - Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

      - Electronic Trip Unit Circuit Breakers: RMS sensing, field-replaceable rating plug, with the following field-adjustable settings:

        - Instantaneous trip.

        - Long- and short-time pickup levels.

        - Long- and short-time time adjustments.

        - Ground-fault pickup level, time delay, and I2t response.

      - Current-Limiting Circuit Breakers: Frame sizes 400A and smaller; let-through ratings less than NEMA FU 1, RK-5.

      - Integrally Fused Circuit Breakers: Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

Refer to Electrical System Design Criteria. Select 5mA for personnel protection, or 30mA for equipment protection.

      - GFCI Circuit Breakers: Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

      - Molded-Case Switch: Molded-case circuit breaker without trip units.

    - Molded-Case, Circuit-Breaker Features and Accessories: Standard frame sizes, trip ratings and number of poles, with lockout mean accommodating up to three padlocks.

      - Lugs: Mechanical style, suitable for number, size, trip ratings, and material of conductors.

      - Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

      - Ground-Fault Protection: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

      - Communication Capability: [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system.

      - Shunt Trip: 120V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

      - Undervoltage Trip: Set to operate at 35 to 75 percent of rated voltage [without intentional] [with field-adjustable 0.1- to 0.6-second] time delay.

      - Auxiliary Switch: [One SPDT switch] [Two SPDT switches] with “a” and “b” contacts; “a” contacts mimic circuit-breaker contacts; “b” contacts operate in reverse of circuit-breaker contacts.

      - Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

      - Zone-Selective Interlocking: Integral with electronic trip unit, for interlocking ground-fault protection function.

    - Fusible Switch: NEMA KS 1, Type HD, clips to accommodate specified fuses with lockable handle.

  - MOTOR-CONTROL CENTER ACCESSORIES

    - Devices shall be factory installed in controller enclosure, unless otherwise indicated.    Comply with NEMA ICS 5.

Delete paragraphs and associated subparagraphs below if not applicable. Coordinate with Drawings.

    - Push-Buttons, Pilot Lights, and Selector Switches: NEMA ICS 2, heavy-duty, industrial oil-tight type.

      - Include push-to-test pilot lights, red “running” and green “ready”, mounted in front panel of each module.

    - Stop and Lockout Push-Button Station: Momentary-break, push-button station with a factory-applied hasp arranged so padlock can be used to lock push button in depressed position with control circuit open.

    - Control Relays: Auxiliary and adjustable time-delay relays.

    - Elapsed Time Meters: Heavy duty with digital readout in hours.

Edit following paragraph to fit project requirements. F&I specifies EATON for electrical metering equipment, No Equal for projects at the Airport. Competition waiver to be submitted to CPO for Eaton electrical metering equipment to be the only approved product for STIA or existing waiver verified, and include the following paragraph and subparagraphs.

    - Multifunction Digital-Metering Monitor: UL-listed, microprocessor-based unit suitable for three- or four-wire systems, compatible with Eaton, No Equal, “IQ Data” series over IMPACC system network, and with the following features:

      - Inputs from sensors or 5A current-transformer secondaries, and potential terminals rated to 600V.

      - Switch-selectable digital display of the following:

        - Phase Currents, Each Phase

        - Phase-to-Phase Voltages, Three Phase

        - Phase-to-Neutral Voltages, Three Phase

        - Three-Phase Real Power

        - Three-Phase Reactive Power

        - Power Factor

        - Frequency

        - Integrated Demand with Demand Interval Selectable from 5 to 60 Minutes

      - Mounting: Display and control unit flush or semiflush mounted in instrument compartment door.

    - Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays as required by engineering considerations: Solid-state sensing circuit with isolated output contacts for hard-wired connections. Provide adjustable undervoltage, overvoltage, and time-delay settings.

    - Space heaters, with NC auxiliary contacts, to mitigate condensation in enclosures installed outdoors or in unconditioned interior spaces subject to humidity and temperature swings.

Use paragraph below with three external current transformers.

    - Current-Sensing, Phase-Failure Relays: Solid-state sensing circuit with isolated output contacts for hard-wired connection; arranged to operate on phase failure, phase reversal, current unbalance of from 30 to 40 percent, or loss of supply voltage; with adjustable response delay.

    - Spare control-wiring terminal blocks, unwired.

    - Spare-Fuse Cabinet: Identified cabinet with hinged lockable door.

  - FACTORY FINISHES

    - Finish: Manufacturer’s standard paint applied to factory-assembled and tested controllers before shipping.

  - PROVISIONS FOR EXPANSION

    - Make provisions for extending horizontal bus for addition of vertical sections in future.

- EXECUTION

  - EXAMINATION

    - Examine areas to receive motor-control centers for compliance with dedicated working space requirements of NEC Article 110-26, installation tolerances and other conditions affecting performance.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Floor Mounting Controllers: Install motor-control centers on 3-1/2-inch nominal thickness concrete bases rated for 3000psi minimum. Comply with Section 03 30 00 - Cast-in-Place Concrete.

      - Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch centers around the full perimeter of concrete base.

      - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

      - Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

      - Install anchor bolts to elevations required for proper attachment to supported equipment.

    - Comply with mounting and anchoring requirements specified in Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

    - Controller Fuses: Install fuses in each fusible switch. Comply with requirements in Section 26 28 13 - Fuses. Arrange fuses so rating information is readable without removing fuse.

    - Install heaters in thermal-overload relays. Select heaters based on actual nameplate full-load amperes after motors have been installed.

    - Install, connect, and fuse thermal-protector monitoring relays furnished with motor-driven equipment.

    - Install power factor correction capacitors. Connect to the line OR load side of overload relays. If connected to the load side of overload relays, adjust overload heater sizes to accommodate the reduced motor full-load currents.

    - Comply with NECA 1.

  - CONTROL WIRING INSTALLATION

Delete this Article if not applicable or if remote control or indication is not required.

    - Install wiring between motor-control devices according to Section 26 05 19 - 600 Volt or Less Wire and Cable.

    - Bundle, train, and support wiring in enclosures.

    - Connect hand-off-automatic switch and other automatic-control devices where available.

      - Connect selector switches to bypass only manual- and automatic-control devices that have no safety functions when switch is in hand position.

      - Connect selector switches with motor-control circuit in both hand and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

      - Provide auxiliary switch operated by disconnect switch mechanism to remove all foreign control power when disconnect switch is open.

  - CONNECTIONS

Coordinate conduit installations and specialty arrangements with schematics on Drawings and with requirements specified. If Drawings are explicit enough, these requirements may be reduced or omitted.

    - Conduit installation requirements are specified in other Division 26 Electrical Sections. Drawings indicate general arrangement of raceways.

    - Ground equipment.

    - Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A and UL 486B.

      - Mark lugs after torquing with red paint such that paint will be visibly disturbed if lugs are disturbed.

  - IDENTIFICATION

    - Identify motor-control center, motor-control center components, and control wiring according to Section 26 05 53 - Electrical Identification.

    - Label motor control center with engraved laminated-plastic nameplate with equipment designation, power source, source location and voltage.

    - Label each motor-control center compartment. Indicate equipment identification, location, and horsepower.

    - Provide typed label inside each motor controller door identifying nameplate horsepower, full-load amperes, code letter, service factor and voltage/phase rating.

    - Equipment used in emergency systems shall be labeled “Suitable for use on emergency systems” per NEC 700-3.

Show specific information to be included in framed instructions on Drawings. If not required, delete below.

    - Operating Instructions: Frame printed operating instructions for motor-control centers, including control sequences and emergency procedures. Fabricate frame of finished metal and cover instructions with clear acrylic plastic. Mount on front of motor-control centers.

  - FIELD QUALITY CONTROL

    - Manufacturer’s Field Service: Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including pre-testing and adjusting solid-state controllers.

    - Prepare for acceptance tests as follows:

      - Remove all blocking used for shipment.

      - Test insulation resistance for each motor-control center element, bus, and component, connecting supply, feeder, and control circuit. Use a 500-Volt Megger for 208- and 240-Volt systems, and a 1000-Volt Megger for 480-Volt systems.

      - Test continuity of each circuit and equipment ground.

      - Verify proper rating of overcurrent protective devices.

      - Verify correct conductor color-coding.

      - With motor disconnected, energize control circuits and test for correct functioning.

        - Control switch test:

          - Inspect all contacts and shunts. Clean contacts if required.

          - Operate switch and note that all design functions are performed in proper sequence.

        - Check all auxiliary contacts for correct arrangement with coil de-energized (normally open or normally closed).

      - Check all motors for proper phase rotation.

    - Testing: Perform the following field quality-control testing:

      - Perform each electrical test and visual and mechanical inspection indicated in NETA ATS, Section 7.16.1.

      - Certify compliance with test parameters.

      - Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

    - Test Reports: Prepare a written report to record the following:

      - Test procedures used.

      - Test results that comply with requirements.

      - Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

  - ADJUSTING

Paragraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

    - Set field-adjustable switches and circuit-breaker trip ranges.

    - Set motor circuit protectors as low as possible without causing nuisance tripping.

    - Set motor overloads per manufacturer’s tables for actual motor nameplate full-load amperes.

    - Where motor controllers with CT/Microprocessor overloads are employed, set all adjustable parameters per Engineer’s instructions.

    - Set the taps on reduced-voltage autotransformer controllers as required by the Engineer or the driven load manufacturer’s recommendation.

    - Set field-adjustable switches and program microprocessors for required start and stop sequences in reduced-voltage, solid-state controllers.

    - Program microprocessors in VFCs for required operational sequences, status indications, alarms, event recording, and display features. Clear events memory after final acceptance testing and prior to Substantial Completion.

    - Set field-adjustable circuit-breaker trip ranges as directed by the Engineer of Record.

  - CLEANING

    - Clean controllers internally, on completion of installation, according to manufacturer’s written instructions. Vacuum dirt and debris; do not use compressed air to assist in cleaning.

  - STARTUP SERVICE

    - Engage a factory-authorized service representative to perform startup service.

    - Verify that motor-control centers and components are installed and connected according to the Contract Documents.

    - Verify that electrical wiring installation complies with manufacturer’s submittal and installation requirements in Division 26 Electrical Sections.

    - Complete installation and startup checks according to manufacturer’s written instructions.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Port maintenance personnel to adjust, operate, and maintain motor-control centers.

      - Train Port maintenance personnel a minimum of four hours on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

      - Review data in maintenance manuals. Refer to Section 01 78 23.13 - Operations and Maintenance Data.

      - Schedule training with the Port with at least seven days’ advance notice.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Reference to Other Sections and Sole Source