READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document REQUIRES an approved Competition Waiver per CPO-6 for Systimax Solutions Communication Backbone Cabling (including UTP copper backbone and tie cables, UTP cat 6/6a copper termination hardware, fiber optic cable, fiber optic cable termination and splice hardware) and Horizontal Cables (including optic fiber cable, patch panels, connectors, couplers, UPT copper backbone, data patch panels, blocks, wall plates, boxes, jumper/patch cords).

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Tab) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “General Communications Requirements” Work is shown in the Contract Documents. Section includes, but is not limited to, general requirements for communications and electronic installations for the Port of Seattle facilities. The Work includes:

      - Coordination of all communication design, terminations and labels with Port of Seattle Sea-Tac/Seaport Telecommunications Architectural Review Team (START) and submit a START application.

      - Contacting the Port of Seattle ICT Service Desk at 206-787-3333 to assist with new and existing communication connectivity throughout the Port of Seattle infrastructure plant.

      - Provide and install pathways for Backbone fiber optic and copper cabling.

      - Provide and install pathways for Horizontal fiber optic and copper cabling.

      - Splice/Terminate fiber optic cable in communications rooms and terminate fiber optic cable in stand-alone controllers.

      - Provide testing of communication components and systems to meet Systimax Solutions warranty requirements and/or Port specifications. Coordinate with the Construction Manager for UTP and fiber optic cable testing.

      - Provide and install labels; refer to Section 27 05 53.13 – Communications Standard for Labeling and Nomenclature.

      - Contractor to provide as-built labeling information to Port of Seattle within three (3) days of project completion.

      - Coordinate with the Construction Manager and other contractors for use of existing cable pathways (cable trays and conduits) to install portions of the cabling.

      - Comply with low-voltage grounding specifications in Section 26 05 26 - Grounding.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ANSI/TIA/EIA-568-C, Commercial Building Telecommunications Wiring Standard.

    - ANSI/TIA-569-B Commercial Building Standard for Telecommunications Pathways and Spaces.

    - ANSI/TIA-606-A Administration Standard for Commercial Telecommunications Infrastructure

    - ANSI-J-STD-607-A Commercial Building Grounding (Earthing) and Bonding Requirements for Telecommunications.

    - ANSI/TIA-758-A, Customer-Owned Outside Plant Telecommunications Infrastructure Standard.

    - BICSI (Building Industry Consulting Services International): Comply with the most current editions of the following BICSI manuals:

      - BICSI - Telecommunications Distribution Methods Manual

      - BICSI – Installation Transport Systems Information Manual

      - BICSI – Network Design Reference Design Manual

      - BICSI – Outside Plant Design Reference Manual

      - BICSI – Wireless Design Reference Manual

      - BICSI -Electronic Safety and Security Design Reference Manual

      - Infocomm/BICSI – AV Design Reference Manual

    - Underwriters Laboratories (UL) Cable Certification and Follow-Up Program.

    - National Electrical Manufacturers Association (NEMA)

    - American Society for Testing Materials (ASTM)

    - National Electrical Code (NEC) with applicable edition year

    - National Electrical Safety Code (NESC) with applicable edition year

    - Institute of Electrical and Electronic Engineers (IEEE)

    - UL Testing Bulletin

    - Building Industry Consulting Services International (BICSI) Information Transport Systems Methods Manual (ITSMM)

    - Canadian Standards Association (CSA)

    - ETL Testing Laboratories

    - Federal Communications Commission (FCC)

    - Labor and Industries (L&I)

    - Washington State Department of Labor and Industries

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

  - DEFINITIONS FOR PORT OF SEATTLE INFRASTRUCTURE

    - Unshielded twisted pair cable (UTP cable)

      - The following UTP cables shall be utilized for Port of Seattle HORIZONTAL runs:

        - (2) Data information outlets per Quadplex (use two blanks in bottom outlets for future additions) for desktop/staff within 100 SqFt. or less of office or cubicle space.

          - Over 100 SqFt of Office space, place (2) Quadplex with (2) Data information outlets per Quadplex. Position on opposing walls where possible.

          - Over 100 SqFt of Cubicle space, place (1) Quadplex with (4) Data information outlets per Quadplex if space warrants possibility of multiple users/excessive equipment per cubicle.

          - For standalone equipment locations such as network printers, phones and cameras (2) Data to a Duplex outlet is required. Termination hardware can vary for these applications, but note that field termination to a male RJ-45 will not be accepted.

          - Note to Communication Engineers: Port of Seattle’s move to a Voice over Internet Protocol (VoIP) allows migration off of the need for horizontal voice runs. Any necessary horizontal voice runs can be addressed in the Equipment Room (ER) with addition of a 24 port patch panel in rack to the 110 wall field with 25pr. tie cables. Scale tie cable and panels in ER per Work area estimates for legacy analog voice needs.

        - Data circuits: 4-pair Category 6/6a (Cat 6/6a)

          - Terminate Source (Port Communication Rm.) to Systimax PATCHMAX GS3 GigaSPEED XL Distribution Hardware, No Equal; PM-GS3-[24] or [48]

          - Terminate Destination end to Systimax GigaSPEED XL; MGS400 (Red) information outlet

        - Legacy analog Voice circuits: 4-pair Category 6/6a (Cat 6/6a)

          - Terminate Source (Port Communication Rm.) to Systimax 300pr. 110 wiring block; 110AW2-300.  Utilize 110C connecting blocks.

          - Terminate destination end to Systimax GigaSPEED XL; MGS400 (Yellow) information outlet

      - The following UTP cables shall be utilized for Port of Seattle BACKBONE cable infrastructure

        - Voice circuits (Inside plant only): 25-pair Category 5/5e (Cat 5/5e) use one to four cables to cover 25pr up to 100pr. counts or:

        - Voice circuits (Outside Plant [OSP] applications & high pair count): 100-pair and up Category 3 (Cat 3)

          - Terminate Source (Port Communication Rm.) to Systimax 300pr. 110 wiring block; 110AW2-300. Utilize 110C connecting blocks, (5) C5’s per row.

          - Terminate Destination* to Systimax 110 wiring block; Destination termination equipment varies per application; refer to engineered drawings.

            - (*) Port communication rooms shall use same termination equipment noted in (1) above at the Source and Destination

          - OSP applications shall follow required protector panel setup at each end of cable

        - Data circuits: 4-pair Category 6/6a (Cat 6/6a) for TENANT Demarcation Backbone Equipment panel; minimum (6/6a) Cat 6/6a.

        - Consideration shall be given to other copper install applications where projects fit a scalable need over time or technology demands an adaptable install such as ICT Data Centers. Manufacturer shall offer a certified and tested material; Installed Copper shall provide a minimum 20 year warranty.

    - Fiber Optic infrastructure (FO cable)

      - The following FO cables shall be utilized for Port of Seattle HORIZONTAL applications such as Fiber directly to Equipment or future Fiber to the Desktop needs; minimum fiber to be installed is 6 strands. Strands terminated shall be specified on engineered plans or directed by the Port of Seattle.

        - Fiber Horizontal (FH): 6 strand Singlemode Fiber (SMF) and/or Multimode [62.5 micron] Fiber (MMF)*

- (*) MMF length cap: 550m at 1Gb/s or less and 300m at 10Gb/s or less

          - Terminate Source (Port Communication Rm.) to OFS 144 port 5 Rack Units Fiber Optic Patch Panel with 6 OFS bulkheads. This Fiber Optic Patch Panel accepts the Systimax SC duplex fiber connectors/ adaptors.

          - Destination termination equipment varies per application; refer to engineered drawings.

          - As required, utilize necessary Fiber optic cables, patch panels, splice shelves, adapters, connectors, buffer kits, breakout kits, consumables, and accessories.

          - Consideration shall be given to Air Blown Fiber (ABF) applications where projects fit a scalable need over time or technology demands an adaptable install such as ICT Data Centers. Manufacturer shall have a certified ABF installer program; installers shall have valid certification from ABF Manufacturer. ABF shall have the ability to physically terminate to Systimax patch panel hardware to maintain existing cross connect fiber patch cord usage, architectural aesthetics and end user ergonomics established in the Port of Seattle communication rooms. Installed Fiber shall provide a minimum 20 year warranty.

      - The following Fiber Optic (FO) cables shall be utilized for Port of Seattle BACKBONE applications such as Port backbone additions or new construction of MDR to ER, ER to ER, and ER to TE. Also, Tenant Demarcation Work of ER to Equipment panel or cabinet. Minimum fiber to be installed is 12 strands, fully terminated.

        - Minimum Fiber Backbone (FB): Minimum strand count is 6 strands Singlemode Fiber (SMF) and 6 strands Multimode [62.5 micron] Fiber (MMF)* or 12 strands of SMF. Note: This is the minimum FB for a Tenant Demarcation package

- (*) MMF length cap: 550m at 1Gb/s or less and 300m at 10Gb/s or less

        - Terminate SMF first in any Fiber Optic Patch Panel (FOPP)

        - Terminate MMF following SMF in any FOPP

        - Maximum strand count where a composite (XM) SMF and MMF can share a (72 or 144 port) FOPP is 36/36; Multiple XM fiber bundles may share a FOPP

        - Strand counts over 36 SMF and 36 MMF shall terminate to separate FOPP’s; note that SMF is the Top FOPP followed by MMF in the FOPP below SMF

        - Strand counts may (and should) be higher on the SMF count than the MMF, including in composite backbone cables

          - Terminate Source (Port Communication Rm.) to OFS 144 port 5 Rack Units Fiber Optic Patch Panel with 6 OFS bulkheads. This Fiber Optic Patch Panel accepts the Systimax SC duplex fiber connectors/ adaptors.

          - Destination termination equipment* varies per application; refer to engineered drawings.

- (*) Port communication rooms shall use same termination equipment noted in (1) above at the Source and Destination

          - As required, utilize necessary Fiber optic cables, patch panels, splice shelves, adapters, connectors, buffer kits, breakout kits, consumables, and accessories.

          - Consideration may be given to Air Blown Fiber (ABF) applications where projects fit a scalable need over time or technology demands an adaptable install such as ICT Data Centers. Manufacturer shall have a certified ABF installer program; installers shall have valid certification from ABF Manufacturer. ABF shall have the ability to physically terminate to Systimax patch panel hardware to maintain existing cross connect fiber patch cord usage, architectural aesthetics and end user ergonomics established in the Port of Seattle communication rooms. Installed Fiber shall provide a minimum 20 year warranty.

    - Port of Seattle Communication Space information

      - Main Distribution Rooms (MDR)

        - Follow layout notes for ER’s below and size of the MDR shall meet or exceed the space of an ER (10 ft x 15 ft)

        - The MDR will hold all Backbone tie cables (Fiber and Copper) to all the Equipment rooms within building or small campus. A larger campus or build may require multiple MDR’s.

      - Entrance Facility (EF)

        - Place adjacent to the MDR or within 50 ft connected to MDR with sufficient cable tray and/or four (4) 4” conduits

        - EF to house the Access Providers (AP) equipment secure and separate from Port communications

        - Minimum EF size shall be 4 ft x 6ft; coordinate with local AP(s).

      - Equipment Rooms (ER)

        - ER may be used as an EF and MDR; room size considerations must be addressed to ensure room for growth

        - Preferred ER shall be at least 10 ft x 15 ft to allow for growth and equipment changes throughout life of the ER

        - 18” wide Ladder rack (cable tray) shall circle the rooms interior walls at 6” from wall and at least 8 ft above finished floor

        - Ladder rack shall cross parallel and centered over each row of racks

        - ER preference is two tiers of 18” wide ladder rack separated by 12” from lower ladder rack and maintaining 12” of clearance from ceiling. Top tier is for Backbone cable (except tenant demarcation package) and lower tier is for horizontal cable and tenant demarcation package(s). Two tier ladder rack system is mandatory in a MDR.

        - HVAC required to maintain a room temperature of 70°

        - Equipment Racks: Minimum of three open frame 42 rack unit (RU) equipment racks with a 6” vertical wire manager on ends and between all racks; typical rack setup:

          - Rack one: All Fiber Optic terminations/ FOPP’s

          - Rack two: Active Network Equipment, other powered gear and UPS

          - Rack three: Horizontal copper cable/ CPP’s

        - Wall field shall (WF) support 300pr. 110 type copper patch blocks with three vertical rows:

          - Row one: Port of Seattle Backbone

          - Row two: Tenant demark 25pr cables

          - Row three: Horizontal CAT 6/6a cables

        - Other wall field space considerations:

          - WiFi Cable and equipment; typically one dedicated WF

          - Cable Television cable termination and Distribution

          - Security systems

          - Point of entry of conduits and Cable Trays

          - Door placement; minimum 3ft wide, no floor sill

          - Power panel location

          - Telecommunications Grounding Busbar

      - Equipment rack or cabinet Destination, including use for Tenant Demarcation package; general information:

        - SMALL Tenant Equipment panel is a flush or surface mount 420 Enclosure (42.16” H x 14.3”W x 3.63” D) with a hinged door. Locations for the small panel are typically concessionaires, small office spaces, etc.

          - Tenant equipment and horizontal cable shall terminate in second equipment panel adjacent to or above the Port equipment and connected with (2) 2” conduit. Second equipment box shall be within 12” of Port EQ

          - If Tenant Demarcation exceeds minimum cable infrastructure package, cabling may be pulled through Port EQ panel with one service loop in equipment panel then run to a tenant rack or cabinet for termination. Terminate any cables not needed in tenant rack or cabinet in Port Equipment panel.

        - MEDIUM Tenant Equipment cabinet shall be a surface mount, adjustable swing hinged locking doors for front and rear access (min. size: 24” H [12RU] x 30” deep). Cabinet back shall support conduit entry via multiple knock-outs and allow entire cabinet to swing open for rear accessibility. The medium cabinets are typically for medium to large office spaces where a cabinet can be placed out of working area or industrial areas such as the airport bagwell and ramp spaces, etc.

          - Typical termination setup is a 48 port Systimax GS3 hybrid patch panel with fiber in ports 1-12, copper data in ports 13-18, ports 19-24 future/backbone expansion and 25-48 for tenant horizontal data cables within space. Copper voice terminated to a rack mount 100pr 110 punch down block with pair 1-25 for Port backbone, 26-50 backbone expansion and 51-100 tenant horizontal voice cables within space.

        - LARGE Tenant locations; typically a Head End or Access Point for tenant with multiple leased locations within a Port facility

          - Necessary cable may be pulled through Demarcation panel into tenant rack or cabinet

          - Refer to Sec.4.a.2 above

        - EXTERIOR communication cabinets

          - Outdoor padmount communications terminal cabinet

            - Minimum size: 24”W x 66”H x 30”D

            - Doors front and rear; preferred with 3 point latch and blue construction core

            - Fabricated 0.125” aluminum mill finish; NEMA-3R U.L. enclosure label

              - Facility conditions or Engineer’s drawings may require Stainless steel

            - Top mounted exhaust fan

            - Fan thermostat

            - 120 VAC receptacle

            - 19” rack mount hardware fore and aft; adjustable

        - DEMARCATION Equipment locations shall house Port backbone cable only; minimum amounts listed (with the exception of above noted Medium Equipment Cabinet):

          - 6 or 12 strands of SMF

          - 6 strands of [62.5 micron] MMF or none

          - 6 Category 6/6a

          - 1 Category 5 25pr

          - 1 RG-11 coaxial

            - Layout of termination hardware available within Port Standards

        - Port Equipment location cable is to be considered permanent infrastructure into leased space

        - A minimum of one 2” conduit is placed from Destination Equipment location to the Port of Seattle ER which is located at or under 80m from Tenant.

  - EQUIPMENT CERTIFICATION

    - Listed Equipment: All applicable material, including accessories to the system and including all wire and cable, shall be listed by an approved agency recognized by Washington State Department of Labor and Industries for the use intended i.e., UL, CSA, ETL, etc.

    - Applicable standards compliance: In addition to the L&I approved listing agency, all communication equipment shall meet applicable portions of FCC, TIA/EIA, ANSI, and Tellcordia Technologies (formerly Bellcore) standards for product performance and quality.

  - WARRANTY

    - In addition to the warranty requirements specified in Section 01 78 36 - Warranties and Bonds, the Contractor shall provide an extended Systimax Solutions warranty as specified in Section 27 13 00 - Backbone Cabling Requirements.

    - All installation and maintenance technicians shall be Systimax Solutions certified.

  - RECORD DOCUMENTS

    - Record documents: Prepare record documents in which indicate the following installed conditions:

      - Communication pathways, size and location, for both exterior and interior; and locations of control devices, patch panels, and equipment racks.

      - Equipment locations (exposed and concealed) dimensioned from column lines.

- PRODUCTS - NOT USED

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

- EXECUTION - NOT USED

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Sole Source