READ THIS FIRST

Notice to the Design Engineer; please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document REQUIRES an approved Competition Waiver per CPO-6 for Systimax Solutions Communication Backbone Cabling (including UTP copper backbone and tie cables, UTP cat 6/6a copper termination hardware, fiber optic cable, fiber optic cable termination and splice hardware) and Horizontal Cables (including optic fiber cable, patch panels, connectors, couplers, UPTP copper backbone, data patch panels, blocks, wall plates, boxes, jumper/patch cords).

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Tab) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Communications Systems Equipment Rooms” Work is shown in the Contract Documents. Section includes, but is not limited to, requirements for Communications Systems Equipment Rooms (ER/TC rooms) at the Seattle-Tacoma International Airport.

    - Work described in this section includes providing and installing:

      - Termination Wallboards

      - Termination panels for fiber optic cable and copper cables.

      - Cable runways.

      - Low-voltage grounding systems.

      - Equipment racks.

    - All rack assemblies shall be Seismic Zone D compliant (assume fully loaded with intended equipment.

  - DEFINITIONS

    - Unshielded Twisted Pair cable (UTP cable)

      - The following UTP cable types shall be utilized for data and voice circuits:

        - Data circuits: 4-pair Category 6/6a

        - Voice circuits: 25-pair Category 5/5e

        - Voice circuits: [50-pair] or [100-pair] Category 3

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - CABLE RUNWAY

    - General:  The Contractor shall provide and install cable runways and supports in each communications room (ER/TC room) as shown on the Drawings and specified herein.

    - Cable Runways:  Cable runways shall have the following characteristics, at a minimum:

      - Manufacturer: Subject to compliance with requirements, provide products by one of the following:

        - B-Line.

        - Saunders

        - Or Approved Equal.

      - Type: 1½” tubular stringer trough with removable post

      - Stringers: 3/8” x 1½” ASTM A513 steel tube

      - Rungs:	  ½” x 1” ASTM A513 steel, welded rungs, welded on interior face of stringers at 9” spacing

      - Finish: Yellow zinc dichromate (YZN)

      - Listing compliance:  UL labeled or Washington State Labor and Industry recognized.

      - Retaining posts: Removable cable retaining posts, 7 inch height above stringer, and 14 posts supplied per runway section.

      - Dimensions:18” wide by 119½” long sections

      - UL cross sectional area: 0.40 in2

      - Design factors (2 rails):

        - Area = 0.210 in2

        - Sx = 0.066 in3

        - Ix = 0.050 in4

      - Load ratings: [4 ft span @ 149 lbs/ft], [5 ft span @ 95 lbs/ft], [6 ft span @ 66 lbs/ft], [7 ft span @ 49 lbs/ft], [8 ft span @ 37 lbs/ft].

    - Fittings:

      - General:  Provide fittings necessary for a complete installation, including but not limited to, stringer splices, horizontal tees, support brackets, and standoffs.  Materials shall be UL listed Or listed Approved Equal.

      - Stringer splices:  Heavy duty stringer splice kit, B-Line, Saunders part number SB-2135, Or Approved Equal, ASTM A1011 structural steel, yellow zinc dichromate finish, UL classified, for 1½” single stringers.  Kit shall include two clamps and ¼”-20 hardware, 4 bolts/nuts/lock washers per splice.

      - Horizontal tee splice:  90 degree horizontal tee splice kit, B-Line, Saunders part number SB-2101-A, Or Approved Equal, ASTM A1011structural steel, yellow zinc dichromate finish, UL classified, for 1½” stringers.  Kit shall include two clamps and 3/8”-16 hardware, 1 bolt/nut/lock washer per clamp.

      - Support bracket:  Runway support bracket kit, B-Line, Saunders part number SB-2116-A, Or Approved Equal [for 5/8” all threaded rod (ATR)] or SB-2116-D Or Approved Equal (for ½” ATR) as required, ASTM A1011 structural steel, yellow zinc dichromate finish, for 1½” stringers Or Approved Equal.  Kit shall include two hanger supports and hardware.

      - Standoff supports:  B-Line, Saunders part number SB-2125, Or Approved Equal, provides 12” spacing between decks, for parallel or perpendicular runways, kit includes two angle supports, four clamps, and 3/8”-16 hardware, ASTM A36 structural steel, yellow zinc dichromate finish.

  - UTP COPPER CABLING

    - Provide and install termination blocks, cabling, and accessories as shown on the drawings, and as specified in Section 27 13 00 - Backbone Cabling Requirements.

  - FIBER OPTIC CABLING

    - Provide and install patch panels and accessories as shown on the drawings and as specified in Section 27 13 00 - Backbone Cabling Requirements.  Install fiber optic cabling, to be provided by the Port.

  - GROUNDING SYSTEM AND CONDUCTORS

    - Bonding and grounding shall meet the requirements specified in Section 26 05 26 - Grounding.

  - EQUIPMENT RACKS AND ACCESSORIES

    - General:  Provide and install 19 inch wide EIA standard equipment racks as shown in the drawings and specified herein.  Racks shall be bolted to the floor and seismically braced.  Label all racks with an engraved phenolic label attached to the top rail with screws.

    - Provide galvanized steel plate between floor and rack such that there is no direct contact between aluminum and concrete.

    - Equipment racks:

      - Manufacturer:	 Subject to compliance with requirements, provide products by one of the following:

        - Chatsworth universal rack

        - B-Line,

        - Or Approved Equal.

      - Construction:  	6061-T6 high strength aluminum extrusion, two top angles, self-support base, and heavy-duty assembly hardware.

      - Mounting holes:  Roll-formed for stronger threads, universal 5/8” – 5/8” – ½” alternating hole pattern, holes back and front of side rail flanges, 12-24 threads, fifty 12-24 mounting screws with combination Phillips/slotted heads and pilot points included with each rack.

      - Channels: EIA channel, 3” x 1.265” x ¼” thick flange.

      - Base angles:  	3½” x 6” x 3/8” thick, one pair per rack.

      - Top angles:  	1½” x 1½” x ¼” thick, one pair per rack.

      - Hardware:  Assembly hardware included.

      - Listing:  Washington State Labor and Industry recognized.

      - General dimensions:  	Seven feet high, 19” rack spacing unless otherwise shown on drawings.

  - TERMINATION WALLBOARDS:

    - Communication (ER/TC) rooms shall be furnished with communication distribution backboards and accessories on all wall surfaces.  These products shall be installed in compliance with local, state and federal codes and industry standards.  Coordinate power outlet locations prior to placement of plywood backboards and cable tray.

    - Furnish and install 8-foot x 4-foot x 3/4-inch AC Marine Grade plywood backboards as indicated.  Paint each backboard with two coats of light-gray, non-conductive fire retardant paint.  Backboards shall be free of surface defects such as knots and cracks.  Unless detail drawings illustrate differently, each backboard shall be installed and oriented with the 8-foot dimension vertical.  Each backboard shall be sufficiently anchored to the wall to support the expected load and seismic Zone 4 requirements.

    - Cabling restraints and routes:  Each cable termination location shall be provisioned with industry standard, cable restraint hardware.  Provide sufficient quantities to ensure cables routed on plywood backboards are restrained at intervals not exceeding 1 foot.  All cables shall be routed parallel and perpendicular to communication room floors.  Two types of restraints are required for plywood backboards:

      - 6-inch D-Ring-type cable restraints shall be utilized for backbone and horizontal cabling on the wallboards.

      - Nylon saddles shall be used to secure the 25 pair cables to the backboards.

- EXECUTION

  - INSTALLATION

    - The Contractor shall install system components and appurtenances in accordance with the manufacturer’s installation instructions and as shown on plans and details.

    - Each device shall be mounted such that its horizontal dimension is level and in no case out of level by .03” over 3 feet in any direction.  In cases where more than one device is mounted, they shall be aligned vertically.  Wiring blocks shall be terminated in accordance with the manufacturer’s instructions and recommendations.  Installation of accessories shall be conducted in accordance with the manufacturer’s instructions and recommendations.

    - Fiber and Copper Cables:  Where fiber optic or UTP cable enters an equipment room it shall be neatly bundled and fastened.  All cable runs shall be horizontal or vertical.

    - Contractor shall provide structural support and seismic bracing for cable runways as specified in Section 27 05 28 - Communication Pathways.

    - Contractor shall provide structural support and anchorage for racks and panels as shown on the plans and details.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

10/15/2014 New Section

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2