READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Access Control System” Work is shown in the Contract Documents.

    - This installation shall consist of standalone access controllers (SACs), remote components and communications devices with fully distributed processing (no degraded mode of operation) that can be centrally programmed, monitored, and controlled.

##### The equipment shall include proximity card readers with integral pinpads, audible/visual signal devices, electromagnetic locks, and door contacts, to be installed at the STIA.

##### The portal card access hardware shall interface with the ACS headend, provided by JCI P2000, which is a modular networkable system that provides the capability for complete integration of the security system components.

##### The Contractor shall be required to install all required electrical door hardware for installation of access control on existing security portal as detailed on the Contract Drawings.

##### Contractor shall be required to replace all existing access controllers, card reader interface modules and electromagnetic locks.

##### Section includes:

##### Description of card reader with pinpad for use with the ACS installed at STIA.

##### Balanced magnetic switch for use with access controlled doors.

##### Request-to-exit (REX) switch for use at access controlled doors.

##### Electromagnetic lock for use at access controlled doors.

##### Audio/visual indicator for use at access controlled doors.

##### Junction and terminal interface boxes for use at access controlled doors as required.

##### Intelligent key system

##### Matching lock mechanisms

##### Keys

##### REFERENCES

##### ANSI A156.23 (American National Standards Institute) – Electromagnetic Locks

##### 14 CFR 107.14 (Code of Federal Regulations) – Access Control System

##### NFPA 101 (National Fire Protection Association) – Code for Life Safety from Fire in Buildings and Structures

## SUBMITTALS:

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

###### Sample of each type of card reader with pinpad and mounting hardware, including faceplate, for approval.

###### Sample of each type of balanced magnetic switch and mounting hardware for approval.

###### Sample of each type of REX and faceplate for approval.

###### Sample of each type of electronic locking device for approval.

###### Sample of each type of audio/visual indicator and mounting hardware for approval.

###### Sample of each type of junction and terminal interface box for approval.

###### Sample of each type of access controller and mounting hardware for approval.

###### Sample of each type of Intellikey hardware for approval.

## QUALITY ASSURANCE

##### Equipment shall be UL listed.

##### Contractor shall have performed a minimum of three similar installations.

##### Manufacturer: Manufacturer of the access control devices, proximity card readers and access control panels shall have been engaged in manufacture of the devices for a minimum of 5 years.

##### All equipment shall be new and shall have passed all manufacturer quality assurance procedures.

## DELIVERY, STORAGE, AND HANDLING:

##### As specified in Section 27 05 13 – General Communications Requirements.

## WARRANTY

##### Provide warranty per Section 01 78 36 – Warranties and Bonds.

## MAINTENANCE AND SERVICE

##### Provide maintenance and service per Section 01 78 23.13 - Operations and Maintenance Data.

## system interface requirements

##### Access controller shall provide a signal that is compatible with the existing ACS headend.

##### Card reader with pinpad shall read existing proximity cards in order to ensure system operation.

###### Coordinate with the [Engineer] and [STIA Information Technology Department and the STIA Aviation Maintenance Department to confirm proximity card type].

###### Card reader with pinpad shall be capable of communicating over the existing card reader wiring.

## performance requirements

##### Equipment and devices shall be able to operate in areas of high EMI/RFI emissions.  Specifically, equipment shall be unaffected and fully functional in the airport environment, which includes radio and radar emissions from ground radios, and airport and aircraft equipment, especially from aircraft operating on ramp areas.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

### CARD READER WITH PINPAD

Competition waiver to be submitted to CPO for Johnson Controls Morpho Access OMA520 Series to be the only approved product for STIA, or existing waiver verified.

##### Manufacturer/Model: Morpho Access OMA520 Series, No Equal. [All outdoor card reader stations shall be Morpho/Johnson Control Model OMA 521, No Equal. For all indoor card reader stations shall be Morpho/Johnson Control Model MA 521, No Equal.]

##### Reader locations: Readers shall be located as shown on the Contract Drawings.

##### Card reader with pinpad shall be able to read existing STIA proximity technology cards. The readers shall be dual identification input technology capable (proximity and personal identification number PIN) and suitable for access control, alarm management, and/or relay control.

##### The readers shall be capable of independent operation (keypad only, card only) or in a multifunction mode where two valid IDs (PIN and proximity card) are required. The readers shall recognize multiple encoding schemes. Reader shall be weatherproof. The reader shall be powered by 10 to 28.5 VDC, supplied by the controller or reader interface.

##### Communications protocol shall be compatible between the standalone access controller or reader interface and its associated reader.

##### Reader mounting method: Readers shall be suitable for surface or flush mounting as required. Exposed fasteners shall be tamper resistant. Reader shall be mounted on backboxes as shown on the Contract Drawings.

##### The proximity reader shall have a read range of 5 to 8 inches. The reader shall be able to be mounted with its sides against metal door or window frames. The reader can have a short or long read range and be capable of either uni-directional or bi-directional operation.

##### Reader display and indicators: Reader shall have a visual indicator display. When a valid proximity card is presented to the reader, the normally red LED shall flash green and a beeper shall sound.

##### Color: Submit color samples to the Engineer for approval.

##### Reader response: Reader shall respond to passage requests by generating a signal to the standalone access controller or reader interface.

##### Response time shall be 100 milliseconds or less from the time the reader finishes reading the card information and entry authorization is completed until a visual indicator is illuminated.

##### Operating temperature shall be minus 22 degrees F to plus 150 degrees F.

##### The proximity card shall be read when presented in any orientation or at any angle to the surface.

##### Specifications:

##### Read range: Seven inches typical at 12 VDC. Six inches typical at 5 VDC.

##### Card read speed: Less than 100 milliseconds.

##### Approvals: UL 294 Access Control, FCC Part 15, Class A; CE Mark.

##### Power: 10 VDC to 28 VDC.

##### Lifetime: MTBF 22,000 hours; MTTR 0.5 hour.

##### Temperature: -22 to 150 degrees Fahrenheit.

##### Humidity: 0 to 95% relative humidity, noncondensing.

##### Environment: Indoor and outdoor; fully weatherproof.

### ACCESS CONTROLLER:

Competition waiver to be submitted to CPO for Johnson Controls CK721 Network Controller to be the only approved product for STIA, or existing waiver verified.

##### Manufacturer/Model: Johnson Controls CK721 Network Controller, No Equal.

##### Existing Portals: The Contractor shall install a new dual reader interface at existing access portals utilizing the existing cab

##### New Construction: The Contractor shall install a new controller in the SAC room to communicate directly with the access portal devices for new construction as shown on the Contract Drawings.

##### Balanced magnetic switch/DOOR POSITION SWITCH

##### Acceptable manufacturer/model: Sentrol 2700 series, Securitron, M68 series, Or Approved Equal.

##### The balanced magnetic switches (BMS) and door position switches (DPS) shall be of the same make and models as existing port switches. Acceptable switch models are:

##### Door BMS/DPS: Sentrol 2700 series high security, Securitron MMS, Or Approved Equal.

##### Concealed door BMS/DPS: Sentrol 2750 series high security, Securitron J-1055-04F, Or Approved Equal.

##### Overhead door BMS/DPS: Sentrol 2720 series high security, Securitron M68 series, Or Approved Equal.

##### Gate BMS: Sentrol 2740 series high security, Securitron M62FG-SASM series, Or Approved Equal.

##### System interface: BMS/DPS shall interface and be compatible with standalone access controller or reader interface.

##### The BMS/DPS shall detect a ½ inch or less of separating relative movement between the magnet and the switch housing.

##### Upon detecting such movement, it shall transmit an alarm signal to the standalone access controller or door controller.

##### BMS/DPS subassemblies: the BMS/DPS shall consist of a switch assembly and an actuating magnetic assembly.

##### The magnet assembly shall house the actuating magnet.

##### The switch mechanism shall comprise three independent form-c triple-biased reed contacts wired in single pull double throw (SPDT) configuration.

##### Switch shall have a supervised loop.

##### Switches shall be rated for a minimum lifetime of 10,000,000 operations.

##### Housing: the housings of switches and magnets shall be made of nonferrous metal and shall be weatherproof.

##### Housing (except concealed) shall have three feet of stainless steel armored cable to protect leads.

##### Spacers: spacers shall be of nonferrous material.

##### Mounting hardware: exposed fasteners shall be tamper resistant.

##### Contractor shall fabricate mounts, adapter, etc., to fit existing conditions.

### REQUEST-TO-EXIT SWITCH

Competition waiver to be submitted to CPO for Locknetics Model 603 to be the only approved product for the Port.

##### Acceptable Manufacturer/Model: Locknetics Model 603, No Equal.

##### Function:  REX shall be used for signaling access control system standalone access controller or reader interface to open door lock.

###### Shall be suitable for installation either indoors or outdoor and shall be weatherproof.

###### Switch shall be momentary action with a contact rating of at least 7 amps DC.

###### Pushbutton shall be illuminated and shall have the word “EXIT” printed on the pushbutton, which shall be covered by clear button cover to protect lettering.  The button shall match existing REX color scheme.

        - Pushbutton shall be at least 1-5/8 inches in diameter.

###### Switch shall have a visible indicator that illuminates when the door lock has been disengaged.  Indicator shall be visible outdoors in sunlight.

###### Pushbutton shall be furnished complete with brushed stainless-steel cover plate.

### ELECTROMAGNETIC LOCK

Competition waiver to be submitted to CPO for Locknetics MagForce 350+ series to be the only approved product for the Port.

##### Acceptable Manufacturer/Model:  Locknetics MagForce 350+ series, No Equal.

##### Locks shall meet the requirements of ANSI A156.23.

##### Type:  Surface mounted, UL listed, dual voltage electromagnetic lock; Narrow Line Series 350 as manufactured by Locknetics, No Equal.  Provide type to accommodate door application:

###### Single door outswinging application; Locknetics 350+ series, No Equal.

###### Single door inswinging application; Locknetics 350+ series, No Equal.

##### Holding force:  1,200 pounds.

##### Additional Equipment:

###### Provide magnetic bond sensor.

###### Provide door position sensor.

###### Provide lock cover tamper switch.

##### Provide with required filler plates, angle brackets, adapter brackets, and other mounting accessories.

### PANIC BAR

Competition waiver to be submitted to CPO for Von Duprin Signal Switch RX 33/RX 35series to be the only approved product for the Port.

##### Acceptable Manufacturer/Model:  Von Duprin Signal Switch RX 33/RX 35, No Equal.

##### Type:  Von Duprin Signal Switch RX33/35 model, No Equal.

Competition waiver to be submitted to CPO for Von Duprin model DL-12 to be the only approved product for the Port.

##### Electric Power Transfer Door Loop:  Von Duprin model DL-12, No Equal.

##### Existing Doors:  Provide panic bar with contact to break power at the lock.

##### New Doors: Provide a nonlatching electromechanical release device that allows one-motion egress and meets the requirements of NFPA 101 for exit devices at emergency doors.

### POWER SUPPLIES

##### Summary: power supplies shall be Rack Mounted, with the following configurations:

###### Output Voltage: 24VDC

###### Total Output Current (Power): 18 amp

###### Number of output: 16

###### Class 2 Rated Power Limited Outputs

###### PTC Protected Outputs

###### Output Current (Max per output): 2 amp

###### Input Voltage: 115VAC

###### Individual power LED indicators per channel.

###### Power switch with built-in circuit breaker.

###### Filtered and electronically regulated outputs.

###### Short circuit and thermal overload protection.

###### Removable terminal blocks with locking screw flange

###### UL listed

##### For new access portals provide new power supply(s).

###### Power supplies connected to emergency exits shall have failsafe interface to immediately unlock door upon signal from fire system.

###### New doors shall be individually fused and the power supply shall be configured with 25 percent spare capacity.

###### The number of power supplies shall be as required for complete system operation.

### intercom

Competition waiver to be submitted to CPO for STENTOFON to be the only approved product for STIA, or existing waiver verified.

### Acceptable Manufacturer/Model: STENTOFON Part No. 10006291SMD, No Equal.

### AUDIBLE/VISUAL SIGNAL DEVICE

Competition waiver to be submitted to CPO for Federal Signal model MASS24M to be the only approved product for the Port.

### Acceptable manufacturer/model:  Federal Signal model MASS24M, No Equal.

##### Provide an audio/visual indicator at each new access controlled door.

###### Devices shall activate upon door alarm condition creating an audio and visual indication as described in the Contract Documents.

###### Devices can be silenced remotely via the ACS.

###### Devices must be White, 4-wire for individual control of the horn and strobe with no “FIRE” markings on it.

###### Upon acknowledgement of the alarm by the ACS operator the device shall reset.

###### Audio/Visual indicator shall be a low profile strobe and shall be supplied with all mounting hardware.

###### Sounder/Strobes located outdoors or in environmentally uncontrolled areas shall be rated NEMA 4 device for weather resistance.

###### Strobe lens shall be red and at least 3 inches in diameter but not larger than 4 inches in diameter.

###### Strobe shall not require tools for strobe tube replacement.

###### Tube shall be rated for 7,000 hours of use.

###### Strobe mechanism output shall be at least 2.2 Joules.

###### Contractor shall determine correct type of mount for strobe location.

###### Sounder output shall be at least 99 dB at 10 feet.

###### INTELLIKEY SYSTEM

###### STIA currently has Intellikey equipment installed at the Airport. In order to maintain compatibility with existing locks, programming software, and tools, only Intellikey equipment will be accepted for this project.

Competition waiver to be submitted to CPO for Intellikey Corporation, Quantam Series version 1.6 (update12) to be the only approved product for the Port.

###### Acceptable manufacturer/model: Intellikey Corporation, Quantam Series version 1.6 (update12), No Equal.

###### The equipment supplied must be compatible with the existing STIA Intellikey system (keys, lock, and software).

###### Provide 282 Intellikey keys compatible with the existing system as shown on the drawings.

###### Provide 282 Intellikey locks as appropriate to the door hardware shown on the drawings.

- EXECUTION

#### INSPECTION

##### Perform inspection per Section 27 05 13 – General Communications Requirements.

#### GENERAL INSTALLATION

##### Perform general installation processes per Section 27 05 13 – General Communications Requirements.

##### The Contractor shall provide a detailed schedule identifying door number, physical location, SAC location, and installation schedule for replacement of all existing and new door installation for by the Engineer.

##### The Port of Seattle shall provide new readers for access controlled portals as shown in the Contract Drawings.

###### Contractors shall install new cable and power for new doors as shown on the Contract Drawings.

###### Place card readers 48 inches from floor to center and on latch side of door unless shown or noted otherwise on the contract Drawings.

###### Install readers at portals shown on the Contract Drawings.

###### Install according to manufacturer’s instructions.

###### Securely attach readers plumb and true on the surface they are to be mounted on.  Tamper screws matching other device screws shall be used on all readers.

##### Testing: Test all card readers for card read operation, visual indicator display, correct status display on headend terminal, operation of associated door locks and position door switches. Test shall also identify door group operations and displays are portrayed correctly on the ACS user interface.

###### Deficiencies: Correct all deficiencies detected and retest affected components.

#### Balanced magnetic switch/DOOR POSITION SWITCH INSTALLTION

##### Install BMS/DPS as shown on the Contract Drawings.

##### Device shall consist of two units mounted adjacent to each other in door and frame.

###### Switch unit: Door frame monitored containing magnetic switch.

###### Magnet unit: Door mounted, containing permanent magnet.

##### Contractor shall mount BMS/DPS to sense movement of door (either door leaf in double door configuration).

##### Coordinate BMS/DPS installation with installation of card readers.

##### Interface BMS/DPS to ACS standalone access controller.

##### Testing: Test all BMSs/DPSs by opening door and ensure that an alarm has been annunciated at the central processor alarm annunciation display.

#### request-to-exit switch installation

#### Locate REX so that pushbutton is 48 inches from floor to center and on latch side of door unless shown or noted otherwise on drawings.

#### Interface REX with ACS standalone access controller so that switch activation unlocks door.

#### Set door lock delay as directed by Engineer for each door.

#### Test switch for operation

#### Verify visible indicator lights to indicate door status (unlocked).

#### Verify audible indicator sounds to indicate door status (unlocked).

#### ELECTROMAGNETIC LOCK INSTALLATION

##### Install according to manufacturer’s instructions.

##### Interface with ACS for door unlocking.

###### Interface bond sensor to ACS standalone access controller so that if a bond is not sensed in the “lock” position, an alarm will be generated on the ACS.

##### Test locks for correct actuation with ACS card read.  Test with REX for operation.

##### Test emergency doors for fail safe operation.

#### AUDIBLE/VISUAL SIGNAL DEVICES

##### Install according to manufacturer’s instructions.

##### Interface with ACS for actuation of devices upon alarm door.

##### Test devices at doors for function and correct operation with ACS alarm.

##### INTELLIKEY INSTALLATION

##### Install locks in doors as shown

##### Coordinate installation so that the doors are not left inoperative and without locks installed for a period exceeding 1 hour.

##### Coordinate turnover of keys to STIA with Engineer.

#### testing

##### The Contractor shall provide all personnel, equipment, instrumentation, and supplies necessary to perform all testing.

##### Engineer and Airport representatives will witness all field tests.

- MEASUREMENT AND PAYMENT

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

10/15/2014 New Section, Added Sole Source and Salient Characteristics Note to Part 2

01/29/2015 Revised Sole Source