READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

## summary of work

##### The extent and location of the “CCTV System” Work is shown in the Contract Documents. The Contractor shall provide and install closed circuit camera system as shown on the drawings.

##### The camera shall be compatible with Genetec Omnicast V4.7.

##### The camera shall be on Genetec’s ‘Supported Devices’ list with a certification level of ‘C’ for certified and an ‘Initial Support’ level of 4.5(GA) or higher.

##### The camera shall be of manufacturer’s official product line, designed for commercial/industrial 24/7/365 use.

##### The camera shall be based upon standard components and proven technology using open and published protocols.

## Reference CERTIFICATIONs AND STANDARDs

##### The camera shall carry the following EMC approvals:

###### FCC Part 15 - Subpart B

##### The camera shall meet/exceed relevant parts of the following video standards:

###### SMPTE 296M (HDTV 720p)

##### The camera shall meet the following video compression standards:

###### MPEG-4:

        - ISO/IEC 14496-10 AVC (H.264)

##### The camera shall meet the following networking standards:

###### IEEE 802.3af (Power over Ethernet)

###### IEEE 802.1X (Authentication)

###### IPv4 (RFC 791)

## SUBMITTALS

    - Product Data: For each type of camera, provide dimensions; mounting arrangements; location for conduit entries; shipping and operating weights; and manufacturer’s technical data on features, performance, electrical ratings, characteristics, and finishes.

    - Operations and Maintenance Data: For Cameras, all installed devices, and components to include in operation, and maintenance manuals. In addition to items specified in Section 01 78 23.13 - Operations and Maintenance Data, include the following:

      - Routine maintenance requirements for Cameras and all installed components.

## QUALITY aSSURANCE

##### All camera installation, configuration, setup, program and related Work shall be performed by electronic technicians thoroughly trained by the manufacturer in the installation and service of the equipment provided.

##### All equipment provided shall be backed by a minimum of three years manufacturer warranty.

##### The specified unit shall be manufactured in accordance with ISO 9001.

## ENVIRONMENTAL SUSTAINABILITY

##### The specified unit shall be manufactured in accordance with ISO 14000.

##### The specified unit shall be compliant with 2002/95/EG RoHS and 2002/96/EG WEEE.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

### GENERAL

##### The camera shall:

###### Be designed to provide video streams in HDTV 720p (1280x720) resolution at 30 frames per second using H.264 or Motion JPEG.

###### Be equipped with Day/Night functionality.

###### Include a built-in web server.

###### Be equipped with a slot for SD/SDHC memory card expansion.

###### Be manufactured with a tamper resistant body.

### HARDWARE

##### The camera shall:

###### Use a high quality IR-sensitive progressive scan megapixel sensor.

###### Provide remote focus and zoom.

###### Be equipped with a removable IR-cut filter, providing so-called day/night functionality.

###### The camera/s shall be able to be fitted with lenses to provide the following approximate fields of view:

        - 14’W x 10’H at 20’

        - 12’W x 9’H at 8’

###### Be equipped with a high quality varifocal DC-iris.  Provide pictures down to 0.4 lux while in day mode (with IR-filter in use) and down to 0.10 lux while in night mode (with IR-filter removed).

###### Support memory expansion by providing an available SD/SDHC card slot. The camera shall be compatible with Genetec Omnicast V4.7.

###### The camera shall be on Genetec’s ‘Supported Devices’ list with a certification level of ‘C’ for certified and an ‘Initial Support’ level of 4.5(GA) or higher.

###### The camera shall be of manufacturer’s official product line, designed for commercial/industrial 24/7/365 use.

###### The camera shall be based upon standard components and proven technology using open and published protocols.

### VIDEO

##### Resolution

###### The camera shall be able to deliver at least two individually configurable full frame rate video streams of resolutions up to HDTV 720p over IP networks.

###### Supported video resolutions shall include:

        - 640x480

        - 800x600

        - 1024x768

        - 1280x720 (HDTV 720p)

        - 1280x800

##### Encoding

###### The camera shall:

        - Support Motion JPEG encoding in a selectable range from 1 up to 30 frames per second in all resolutions.

        - Support H.264 encoding in a selectable range from 1 up to 20 frames per second in all resolutions.

        - Be able to provide independently configured simultaneous H.264 and Motion JPEG streams.

        - Support both Constant Bit Rate (CBR) and Variable Bit Rate (VBR) in H.264.

        - Provide configurable compression levels.

##### Transmission

###### The camera shall allow for video to be transported over:

        - HTTP

        - HTTPS

        - RTP

        - RTP over RTSP

        - RTP over RTSP over HTTP

###### The camera shall support Quality of Service (QoS) to be able to prioritize traffic.

##### Image control

###### The camera shall incorporate Automatic and Manual White Balance and an electronic shutter operating, as a minimum in the range 1/6 and 1/10,000 second.

###### The camera shall provide Wide Dynamic Range and backlight compensation with automatic and definable exposure zones.

### aUDIO

##### There is no requirement to support audio.

### fUNCTIONALITY

##### Web server

###### The camera shall contain a built-in web server making video and configuration available to multiple clients in a standard operating system and browser environment using HTTP, without the need for additional software.

##### IP addresses

###### The camera shall support both fixed IP addresses and dynamically assigned IP addresses provided by a Dynamic Host Control Protocol (DHCP) server.

###### The camera shall allow for automatic detection of the Camera when using a PC with an operating system supporting this feature.

###### The camera shall provide support for both IPv4 and IPv6.

##### Event functionality

###### The camera shall be equipped with an integrated event functionality, which can be trigged by:

        - External input

        - Video Motion Detection

        - Schedule

        - Camera tampering

        - Local storage full

###### Response to triggers shall include:

        - Notification, using TCP, SMTP or HTTP

        - Image upload, using FTP, SMTP or HTTP

        - Activating external output

        - Recording to local storage

###### The camera shall provide memory for pre & post alarm recordings.

###### Event functions shall be configurable via the web interface.

##### Protocol support

###### The camera shall incorporate support  for at least IP, HTTP, HTTPS, TCP, ICMP, SNMP (MIB-II), RTSP, RTP, UDP, IGMP, SMTP, FTP, DHCP, ARP, DNS and NTP.

###### The SMTP implementation shall include support for SMTP authentication.

##### Text overlay

###### The Camera shall:

        - Provide embedded on-screen text with support for date & time, and a customer-specific text, camera name, of at least 45 ASCII characters.

        - To ensure accuracy, the camera shall accept external time synchronization from an NTP (Network Time Protocol) server.

        - Provide the ability to apply a privacy mask to the image.

##### Security

###### The camera shall:

        - Support the use of HTTPS, providing the ability to upload signed certificates to encrypt and secure authentication and communication of both administration data and video streams.

        - Support IEEE 802.1X authentication.

        - Provide support for restricting access to pre-defined IP addresses only, so-called IP address filtering.

        - Restrict access to the built-in web server by usernames and passwords at three different levels.

##### API support

###### The camera shall be fully supported by an open and published API (Application Programmers Interface), which shall provide necessary information for integration of functionality into third party applications.

##### Installation and Maintenance

###### The camera shall:

        - Be supplied with Windows-based management software which allows the assignment of IP addresses, upgrade of firmware and backup of the Cameras’ configuration.

        - Support the use of SNMP-based management tools according to SNMP v1, 2c & 3 / MIB-II.

        - Allow updates of the software (firmware) over the network, using FTP or HTTP.

###### All customer-specific settings shall be stored in a non-volatile memory and shall not be lost during power cuts or soft reset.

##### User logs

###### The camera shall:

        - Provide a log file, containing information about the latest connections and access attempts since the unit’s latest restart. The file shall include information about the connecting IP addresses and the time of connecting.

        - Provide a connection list of all currently connected viewers. The file shall include information about connecting IP address, time of connecting and the type of stream accessed.

### CAMERA DIAGNOSTICS

##### The camera shall:

###### Be equipped with LEDs, capable of providing visible status information.  LEDs shall indicate the camera’s operational status and provide information about power, communication with receiver, the network status and the camera status.

### INTERFACES

##### Inputs/Outputs

###### The camera shall be equipped with one digital (alarm) input and one digital output, accessible via a removable terminal block. This input shall be configurable to respond to normally open (NO) or normally closed (NC) dry contacts.

##### Network interface

###### The camera shall be equipped with one 100BASE-TX Fast Ethernet-port, using a standard RJ-45 socket and shall support auto negotiation of network speed (100 MBit/s and 10 MBit/s) and transfer mode (full and half duplex)

### Enclosure

##### The camera enclosure shall include the following:

###### Manufactured in a surface mount, flush mount and pendant dome configurations.

###### Manufactured with a tamper resistant body providing encapsulated electronics

###### Clear and smoked transparent cover

###### IP66-rating

###### NEMA 4X-rating

###### Impact resistance of 2200lbs / 1000kg

###### Thermostat, heater and fan inside the enclosure

###### Fitted with a dehumidifying membrane

###### Removable weather shield

##### The camera enclosure shall provide the ability to adjust the camera modules angle with at least 180º horizontal, 85º vertical and 170º rotation while maintaining an image that is not interfered with by the camera housing.

### Power requirements

##### Power over Ethernet according to IEEE 802.3af - Class 2.

##### Acceptable manufacturer/model: Axis 16 port product, Altronix NetWay16M – Managed PoE Midspan Solution, Or Approved Equal.

### Environmental

##### The camera shall:

###### Operate in a temperature range of 0º C to +50º C (32º F to +122º F).

###### Operate in a humidity range of 20–80% RH (non-condensing).

### other devises

##### Patch Panel

Competition waiver to be submitted to CPO for SYSTIMAX 360-IPR-1100-E-GS3-1U-24 to be the only approved product for the Port, or existing waiver verified.

###### Manufacturer/Model: SYSTIMAX 360-IPR-1100-E-GS3-1U-24, No Equal.

- EXECUTION

#### INSTALLATION

##### The Contractor shall carefully follow instructions in documentation provided by the manufacturer to insure all steps have been taken to provide a reliable, easy-to-operate system.

##### All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

##### All firmware found in products shall be the latest and most up-to-date provided by the manufacturer, or of a version as specified by the provider of the Video Management Application (VMA) or Network Video Recorder (NVR).

##### All equipment requiring users to log on using a password shall be configured with user/site-specific password/passwords. No system/product default passwords shall be allowed.

- MEASUREMENT AND PAYMENT

##### GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

10/15/2014 New Section, Added Sole Source and Salient Characteristics Note to Part 2

01/29/2015 Revised Sole Source