READ THIS FIRST

The Engineer shall verify that the latest version of the Federal Aviation Administration Advisory Circular AC 150/5370-10, “Standards for Specifying Construction Of Airports” and that the latest version of the Federal Aviation Administration, Northwest Mountain Region Revision to AC 150/5370-10, “Standards for Specifying Construction Of Airports” are incorporated into this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Airport Wind Cones (FAA)” Work is shown in the Contract Documents. Provide an airport wind cone, complete in accordance with the applicable provisions of FAA Item L-107, Airport 8-Foot and 12-Foot Wind Cones, attached hereto.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

    - TBD

  - SUBMITTALS

    - Submit materials data in accordance with Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

- NOT USED

- NOT USED

- NOT USED

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

## ITEM L-107 AIRPORT 8-FOOT AND 12-FOOT WIND CONES

## DESCRIPTION

107-1.1	This item shall consist of furnishing and installing an airport wind cone in accordance with these specifications and in accordance with the dimensions, design and details shown in the plans.

The work shall include the furnishing and installation of a support for mounting the wind cone, the specified wire and a concrete foundation. The item shall also include all cable connections, conduit and conduit fittings, the furnishing and installation of all lamps, ground rod and ground connection, the testing of the installation and all incidentals necessary to place the wind cone in operation as a completed unit to the satisfaction of the Engineer.

## EQUIPMENT AND MATERIALS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

107-2.1	GENERAL

a.	Airport lighting equipment and materials covered by Federal Aviation Administration (FAA) specifications shall have the prior approval of the FAA, and are listed in Advisory Circular (AC) 150/5345-1, Approved Airport Equipment.

b.	All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification when requested by the Engineer.

107-2.2	WIND CONES. The 8 foot (240 cm) and 12 foot (3.5 m) wind cones and assemblies shall conform to the requirements of AC 150/5345-27, Specification for Wind Cone Assemblies.

107-2.3	WIRE. Wire in conduit rated up to 5,000 volts shall conform to AC 150/5345-7, Specification for L-824 Underground Cable for Airport Lighting Circuits, for rubber insulated neoprene covered wire, of Fed. Spec. J-C-30, Type RHW, for rubber insulated fibrous covered wire. For ratings up to 600 volts, thermoplastic wire conforming to Fed. Spec. J-C-30, Types TW, THW and THWN, shall be used. The wires shall be of the type, size, number of conductors and voltage shown in the plans or in the proposal.

107-2.4	CONDUIT. Rigid steel conduit and fittings shall conform to the requirements of Underwriters Laboratories Standards 6, 514 and 1242.

107-2.5	CONCRETE. The concrete for foundations shall be proportioned, placed and cured in accordance with Item P-610, Structural Portland Cement Concrete.

107-2.6	PAINT

a.	Red lead priming paint for un-galvanized metal surfaces and the mixing thereof, shall conform to the 97% grade specified in ASTM D83. The red lead shall be furnished in paste form and delivered to the job in the original unbroken packages bearing the maker's name and brand designation.

b.	Priming paint for galvanized metal surfaces shall be zinc dust-zinc oxide primer paint conforming to Fed. Spec. TT-P-641. If necessary, add not more than 1/2 pint (0.06 liter) of turpentine to each gallon (liter).

C.	Orange paint for the body and the finish coats on metal and wood surfaces shall consist of a ready-mixed non-fading paint meeting the requirements of Fed. Spec. TT-P-59. The color shall be in accordance with Federal Standard 595, Aviation Gloss Orange Number 12197.

d.	White paint for body and finish coats on metal and wood surfaces shall be ready-mixed paint conforming to Fed. Spec. TT-P-102.

e.	Priming paint for wood surfaces shall be mixed on the job by thinning the above specified aviation-orange or white paint by adding 1/2 pint (0.06 liter) of raw linseed oil to each gallon (liter).

## CONSTRUCTION METHODS

107-3.1	INSTALLATION. The hinged support or hinged pole shall be installed on a concrete foundation as shown in the plans.

107-3.2	COUNTERWEIGHT. The Contractor shall furnish and install a counterweight on the hinged support for the 12 foot (3.5 m) wind cone. The counterweight may consist of lead weights which may be furnished with the “A”-frame assembly or it may consist of concrete poured around the bottom of the hinged support. Where concrete is used, the counterweight shall be approximately 12 inches (300 mm) wide by 24 inches (600 mm) deep and should weigh approximately 500 pounds (230 kg). The counterweight should be 25 to 50 pounds (10 to 20 kg) less than the weight needed to balance the assembly. The counterbalancing should operate to the satisfaction of the Engineer.

107-3.2	ELECTRICAL CONNECTION. The Contractor shall furnish all labor and materials and shall make complete electrical connections in accordance with the wiring diagram furnished with the project plans.

If underground cable from the transformer vault to the wind cone site and duct for this cable installation under paved areas is required, the cable and duct shall be installed in accordance with and paid for by linear foot measurement as described in Item L-108, Installation of Underground Cables for Airports and Item L-110, Installation of Airport Underground Electrical Duct.

107-3.4	BOOSTER TRANSFORMER. If shown in plans or specified in job specifications, a booster transformer to compensate for voltage drop to the lamps shall be installed in a suitable weatherproof housing. The booster transformer shall be installed as indicated in the plans and described in the proposal. If the booster transformer is required for installation in the transformer vault, it shall be installed in accordance with and paid for as described in Item L-109, Installation of Airport Transformer Vault and Vault Equipment.

107-3.5	GROUND CONNECTION AND GROUND ROD. The Contractor shall furnish and install a ground rod, grounding cable and ground clamps for grounding the “A”-frame of the 12 foot (3.5 m) assembly or pipe support of the 8 foot (240 cm) support near the base. The ground rod shall be of the diameter and length specified in the plans and shall be copper or copper clad. The ground rod shall be driven into the ground adjacent to the concrete foundation so that the top is at least 6 inches (150 mm) below grade. The grounding cable shall consist of No. 8 AWG bare stranded copper wire or larger and shall be firmly attached to the ground rod by means of a ground connector or clamp. The other end of the grounding cable shall be securely attached to a leg of the “A”-frame or to the base of the pipe support with non-corrosive metal and shall be of substantial construction. The resistance to ground shall not exceed 25 ohms.

107-3.6	PAINTING. Three coats of paint shall be applied (one prime, one body and one finish) to all exposed material installed under this item except the fabric cone, obstruction light globe and lamp reflectors. The wind cone assembly, if painted on receipt, shall be given one finish coat of paint in lieu of the three coats specified above. The paint shall meet the requirements of Fed. Spec. TT-P-59. The color shall be in accordance with Federal Standard 595, Aviation Gloss Orange Number 12197.

107-3.7	LAMPS. The Contractor shall furnish and install four 200 watt, 115 volt general lighting service lamps in the reflectors for the 12 foot (3.5 m) cone or four 150 watt, 115 volt lamps for the 8 foot (240 cm) cone. A clear 100 watt, 107 watt, or 116 watt, 115 volt traffic signal lamp with a medium screw base, or a 100 watt. A 21 bulb, 115 volt, medium pre-focus base lamp shall be furnished and installed in the obstruction light as required.

107-3.8	CHAIN AND PADLOCK. The Contractor shall furnish and install a suitable operating chain for lowering and raising the hinged top section. The chain shall be attached to the pole support in a manner to prevent the light fixture assembly from striking the ground in the lowered position.

A padlock shall also be furnished by the Contractor on the 8 foot (240 cm) wind cone for securing the hinged top section to the fixed lower section. Keys for the padlock shall be delivered to the Engineer.

## METHOD OF MEASUREMENT

107-4.1	The quantity to be paid for shall be the number of wind cones installed as completed units in place, accepted and ready for operation.

## BASIS OF PAYMENT

107-5.1	Payment will be made at the contract unit price for each completed and accepted job. This price shall be full compensation for furnishing all materials and for all preparation, assembly and installation of these materials, and for all labor, equipment, tools and incidentals necessary to complete this item.

Payment will be made under:

Item L-107-5.1 - 12-Foot (3.5 m) Wind Cone, in place--per unit

Item L-107-5.2 - 8-Foot (240 cm) Wind Cone, in place--per unit

## MATERIAL REQUIREMENTS

| ASTM D83 | 97% grade |
| --- | --- |
| ASTM D83 | Red Lead Pigment |
| Advisory Circular (AC) 150/5345-1 | Approved Airport Equipment |
| Federal Aviation Administration |  |
| AC 150/5345-7 | Specification for L-824 Underground Cable for Airport Lighting Circuits |
| AC 150/5345-27 | Specification for Wind Cone Assemblies |
| FAA Item L-107 | Airport 8 Foot and 12 Foot Wind Cones |
| Item L-107-5.112 | Foot (3.5 m) Wind Cone, in place--per unit |
| Item L-107-5.28 | Foot (240 cm) Wind Cone, in place--per unit |
| Item L-108 | Installation of Underground Cables for Airports |
| Item L-109 | Installation of Airport Transformer Vault and Vault Equipment, |
| Item L-110 | Installation of Airport Underground Electrical Duct, |
| Item P-610 | Structural Portland Cement Concrete, |
| Fed. Spec.J-C-30 | Cable and Wire, Electrical (Power, Fixed Installation), |
| Fed. Spec. J-C-30 | Type RHW, for rubber insulated fibrous covered wire, for rubber insulated neoprene covered wire |
| Fed. Spec.TT-P-59 | Paint: Ready-mixed, International Orange, |
| Fed. Spec.TT-P-102 | Paint, Oil: Titanium-Lead-Zinc and Oil, Exterior, Ready-mixed, White and Light Tints, |
| Fed. Spec.TT-P-641 | Primer, Paint; Zinc Dust-Zinc Oxide, |
| Fed. Spec.W-P-115 | Panel, Power Distribution, |
| Federal Standard 595 | Aviation Gloss Orange Number 12197, |
| Underwriters Laboratories Standard 6 | Rigid Metal Conduit |
| Underwriters Laboratories Standard 514 | Fittings For Conduit and Outlet Boxes |
| Underwriters Laboratories Standard 1242 | Intermediate Metal Conduit |

End of Item