READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

This section does not include specifications for Marine installations.

    - The extent and location of “Raceways and Boxes” Work is shown in the Contract Documents. This section includes raceways, fittings and boxes for electrical wiring.

Edit lists below to suit Project.

      - Raceways include the following:

        - Rigid Metal Conduit (RMC).

        - Aluminum Conduit (RMC).

        - Electrical Metallic Tubing (EMT).

        - Flexible Metal Conduit (FMC).

        - Liquidtight Flexible Metal Conduit (LFMC)

        - Rigid Nonmetallic Conduit (RNC).

        - Metal Wireway.

        - Nonmetallic Wireway.

        - Surface Metal Raceway.

        - Surface Nonmetallic Raceway.

        - Strut-type Channel Raceway.

      - Boxes include the following:

        - Device boxes.

        - Floor boxes.

        - Outlet boxes.

        - Pull and junction boxes.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ANSI C80.1 - Rigid Steel Conduit, Zinc Coated

    - ANSI C80.3 - Electrical Metallic Tubing, Zinc Coated

    - ANSI C80.5 - Rigid Aluminum Conduit

    - NECA (National Electrical Contractors Association) - National Electrical Installation Standards

    - NEMA FB 1 (National Electrical Manufacturers Association) - Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, Electrical Metallic Tubing (EMT) and Cable.

    - NEMA OS 1 (National Electrical Manufacturers Association) - Sheet-steel Outlet Boxes, Device Boxes, Covers, and Box Supports

    - NEMA OS 2 (National Electrical Manufacturers Association) - Nonmetallic Outlet Boxes, Device Boxes, Covers and Box Supports

    - NEMA TC 3 (National Electrical Manufacturers Association) - PVC Fittings for Use with Rigid PVC Conduit and Tubing

    - NEMA 250 (National Electrical Manufacturers Association) - Enclosures for Electrical Equipment (1000 Volts Maximum)

    - NFPA 70 (National Fire Protection Association) - National Electrical Code

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: For surface raceways, Conduit, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.

      - Shop Drawings: For custom enclosures and cabinets. Include plans, elevations, sections, and attachment details.

      - Coordination Drawings: Conduit routing plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of items involved:

        - Structural members in paths of conduit groups with common supports.

        - HVAC and plumbing items and architectural features in paths of conduit groups with common supports.

      - Surface raceways.

      - Qualification Data: for Professional Engineer.

      - Seismic Qualification Certificates: For enclosures, cabinets, and conduit racks and their mounting provisions, including internal components, from manufactures.

        - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

        - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

        - Detailed description of conduit support devices and interconnections on which the certification is based and their installation requirements.

      - Conduit, Wireways and fittings.

      - Floor boxes.

  - QUALITY ASSURANCE

    - Listing and Labeling: Provide raceway and boxes that are Listed and Labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to the Authority Having Jurisdiction, and marked for intended use for the location and environment in which they are installed.

    - Comply with NECA’s “National Electrical Installation Standards.”

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

  - COORDINATION

    - Raceway and boxes are shown on drawings in approximate locations unless dimensioned. Locate raceway and boxes as shown and at other locations where required for splices, taps, wire pulling, equipment connections, and compliance with regulatory requirements. Coordinate layout and installation of raceways and boxes with other construction elements to ensure adequate headroom, working clearance, and access, and to complete the wiring system.

    - Galvanized electrical equipment installed exposed outdoors shall be painted with a minimum 3 mil coating of paint to prevent zinc runoff to the stormwater system.  Paint application by manufacturer is preferred to field painting for coverage and quality.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - METAL CONDUIT AND TUBING

    - Rigid Steel Conduit (RMC): ANSI C80.1.

    - Rigid Aluminum Conduit (RMC): ANSI C80.5. For use with 400Hz systems only.

    - Electrical Metallic Tubing (EMT): ANSI C80.3.

    - Intermediate Metallic Conduit (IMC) is not allowed.

    - Flexible Metal Conduit (FMC): Zinc-coated non-reduced wall steel.

    - Liquidtight Flexible Metal Conduit (LFMC): Flexible steel conduit with PVC jacket.

    - Fittings: NEMA FB 1; compatible with conduit/tubing materials.

      - Fittings for EMT: Steel Compression type. Setscrew type is not allowed.

  - NONMETALLIC CONDUIT AND TUBING

    - Rigid Nonmetallic Conduit (RNC/PVC): NEMA TC 2, Schedule 40 or 80 PVC.

    - RNC Fittings: NEMA TC 3; match to conduit or conduit/tubing type and material.

  - METAL WIREWAYS

    - Material: Sheet metal size and shape as indicated on drawings. Comply with UL 870 and NEMA 250, Type 1 unless otherwise indicated.

      - Metal wireways installed outdoors shall be listed and labeled as defined in NFPA 70 (NEC).

    - Fittings and Accessories: Include couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for a complete system.

    - Select features, where not indicated, as required to complete wiring system and to comply with NFPA 70 (NEC).

    - Wireway Covers: Hinged type.

    - Finish: Manufacturer’s standard enamel finish, ANSI 61 gray color.

  - NONMETALLIC WIREWAYS

    - Description: Fiberglass polyester, extruded and fabricated to size and shape indicated, with no holes or knockouts. Cover is gasketed with oil-resistant gasket material and fastened with captive screws treated for corrosion resistance. Connections are flanged, with stainless-steel screws and oil-resistant gaskets.

Select paragraph above or below.

    - Description: PVC plastic extruded and fabricated to size and shape indicated, with snap-on cover and mechanically coupled connections using plastic fasteners.

    - Fittings and Accessories: Include couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for a complete system.

    - Select features, unless otherwise indicated, as required to complete wiring system and to comply with NFPA 70 (NEC).

  - SURFACE RACEWAYS

    - Surface Metal Raceways: Galvanized steel with snap-on covers complying with UL 5. Finish with manufacturer’s standard rust inhibiting prime coating and standard enamel finish in color selected by Architect.

    - Surface Nonmetallic Raceways: 2-piece construction, complying with UL 5A, manufactured of rigid PVC compound with matte texture and manufacturer’s standard enamel finish in color selected by Architect.

    - Types, sizes, and channels as indicated and required for each application, with fittings that match and mate with raceways.

  - OUTLET AND DEVICE BOXES

    - General Requirements for Boxes, Enclosures, and Cabinets: Boxes, enclosures, and cabinets installed in wet locations shall be listed for use in wet locations.

    - Sheet Metal Outlet and Device Boxes: Comply with NEMA OS 1 and UL 514A.

    - Cast-Metal Outlet and Device Boxes: Comply with NEMA FB 1, ferrous alloy, Type FD, with gasketed cover and threaded hubs.

    - Nonmetallic Outlet and Device Boxes: Comply with NEMA OS 2 and UL 514C.

    - Luminaire Outlet Boxes: Nonadjustable, designed for attachment of luminaire weighing 50 lb. Outlet boxes designed for attachment of luminaires weighing more than 50 lb. shall be listed and marked for the maximum allowable weight.

    - Box extensions used to accommodate new building finishes shall be of same material as recessed box.

    - Device Box Dimensions: 4 inches square by 2-1/8 inches deep.

  - FLOOR BOXES

    - Metal Floor Boxes – for new concrete floors:

      - Material: Cast metal.

      - Type: Fully adjustable.

      - Shape: Rectangular.

      - Listing and Labeling: Metal floor boxes shall be listed and labeled as defined in NFPA 70 (NEC), by a qualified testing agency, and marked for intended location and application.

  - PULL AND JUNCTION BOXES

    - Small Sheet Metal Boxes: NEMA OS 1, galvanized steel.

    - Cast-Metal Boxes: NEMA FB 1, cast aluminum with gasketed cover, ground flange and stainless steel cover screws.

    - Sheet Steel Gauge Requirements (Any Direction):

      - Less than 24”: 14 USS gauge.

      - 24” to 36”: 12 USS gauge.

      - 36” or larger: 10 USS gauge.

  - ENCLOSURES AND CABINETS

    - Hinged 110o Swing Opening Cover Enclosures:  NEMA 250, Type 1, [steel] OR [PVC or fiberglass] enclosure with continuous hinge cover and flush latch, finished [inside and out with manufacturer’s standard enamel] OR [inside with radio-frequency paint].

    - Cabinets:

      - NEMA 250, Type 3R, 4X or 12 galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

      - Hinged door in front cover with flush latch and concealed hinge.

      - Key latch to match panelboards.

      - Metal barriers to separate wiring of different systems and voltage.

    - Panelboard Enclosures:  Panelboard enclosure criteria are addressed separately.  Refer to Criteria Section 26 09 26 - Panelboards.

    - Metal Enclosures: Steel, finished inside and out with manufacturer's standard enamel.

    - Nonmetallic Enclosures: Plastic or Fiberglass.

    - Interior Panels: Steel; all sides finished with manufacturer's standard enamel or with radio-frequency paint].

  - TERMINAL BLOCKS

    - Minimum 600-volt rating for 480-volt circuits

    - Clamp or screw terminals sized for maximum conductor size

    - Separate connection point for each conductor

    - 10% spare terminal points

    - Individual identification for each terminal block

    - Phenolic block separators or barriers shall be used to isolate low-voltage and control terminations from analog and DC circuits.

  - HANDHOLES AND BOXES FOR EXTERIOR UNDERGROUND WIRING

    - Description:

      - General Requirements for Handholes and Boxes:

        - Boxes and handholes for use in underground systems shall be designed and identified as defined in NFPA 70 (NEC), for intended location and application.

        - Boxes installed in wet areas shall be listed and labeled as defined in NFPA 70 (NEC), by a qualified testing agency, and marked for intended location and application.

        - Comply with handhole requirements in Section 26 05 43 Underground Ducts and Manholes.

      - Fiberglass Handholes and Boxes: Fiberglass Handholes and Boxes: Molded of fiberglass-reinforced polyester resin, with frame and covers of reinforced concrete or cast iron.

        - Standard: Comply with SCTE 77.

        - Color of Frame and Cover: Gray.

        - Configuration: Designed for flush burial with closed bottom unless otherwise indicated.

        - Cover: Weatherproof, secured by tamper-resistant locking devices and having structural load rating consistent with enclosure and handhole location.

        - Cover Finish: Nonskid finish shall have a minimum coefficient of friction of 0.50.

        - Cover Legend: Molded lettering, "ELECTRIC.".

        - Conduit Entrance Provisions: Conduit-terminating fittings shall mate with entering ducts for secure, fixed installation in enclosure wall.

        - Handholes 18 Inches Wide by 24 Inches Long and Larger: Have inserts for cable racks and pulling-in irons installed before concrete is poured.

      - Manufacturers:

        - Armorcast Products Company.

        - Carson Industries LLC.

        - NewBasis.

        - Nordic Fiberglass, Inc.

        - Oldcastle Precast, Inc.; Christy Concrete Products.

        - Quazite: Hubbell Power System, Inc.; Hubbell Power Systems.

        - Or Approved Equal.

- EXECUTION

  - EXAMINATION

    - Examine surfaces to receive raceways and boxes for compliance with installation tolerances and other conditions affecting performance of raceway installation. Do not proceed with installation until unsatisfactory conditions have been corrected.

  - EXISTING WORK

Delete this article if existing construction is not affected or if there is none on the project. Edit to meet project requirements.

    - Remove exposed abandoned raceway, including abandoned raceway above accessible ceiling finishes. Cut raceway flush with walls and floors and patch surfaces.

    - Remove concealed abandoned raceway to its source.

    - Disconnect abandoned outlets and remove devices. Remove abandoned outlets if raceway servicing them is abandoned and removed. Provide blank cover for abandoned outlets which are not removed.

    - Ensure access to existing boxes and other installations which remain active and which require access. Modify installation or provide access panel as appropriate.

    - Extend existing raceway and box installations using materials and methods as specified.

    - Clean and repair existing raceway and boxes which remain or are to be reinstalled.

  - WIRING METHODS

Edit materials and methods to suit Project. Coordinate with Section 26 05 19 - 600 Volt or Less Wire and Cable.

    - Outdoors: Use the following wiring methods:

      - Exposed: Rigid steel conduit (RMC).

        - Use of aluminum RMC is limited to 400 Hz, grounding, and special applications.

      - Concealed: PVC Schedule 40 is the standard for use in rebar reinforced duct banks. Aluminum is excluded. Rigid steel conduit (RMC) shall be used under roadways in non-reinforced duct banks.

      - Underground: See Section 26 05 43 – Underground Ducts and Manholes.

      - Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment): Liquidtight flexible metal conduit (LFMC).

Modify box types for the specific project environments. NEMA 3R shall be used in non-corrosive, non-dusty outdoor environments. NEMA 4 shall be used in interior or exterior dusty or dirty environments. NEMA 4X shall be used in interior and exterior corrosive or marine environments.

      - Boxes: Type shall be as specified in the drawings. NEMA 3R in non-corrosive, non-dusty outdoor locations, NEMA 4 in interior or exterior dusty or dirty locations, NEMA 4X in interior and exterior corrosive locations.

    - Indoors: Use the following wiring methods:

      - Aluminum RMC limited to 400Hz, grounding and special applications. Aluminum conduit, boxes or fittings shall not come in contact with concrete. Provide non-metallic sleeve where aluminum conduit passes through concrete structure.

      - Exposed: Rigid steel conduit (RMC) or electrical metallic tubing (EMT).

        - Rigid steel conduit shall be used up to 8 feet above finish floor in traffic areas subject to damage, such as in the conveyor, shop and ramp areas.

      - Concealed: Rigid steel conduit (RMC) or electrical metallic tubing (EMT).

        - Use EMT in sizes 1/2” to 1-1/2” only, except larger EMT may be used for communications wiring such as telephone or fire alarm systems.

        - Power raceways 2-inches and larger shall be rigid steel conduit.

      - Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment): Flexible metal conduit (FMC), except in wet or damp locations, use liquidtight flexible metal conduit (LFMC).

      - Damp or Wet Locations: Rigid steel conduit (RMC).

Some editing to that noted in paragraph and subparagraphs is acceptable with F & I approval.

      - Boxes: NEMA 250, Type 1, except as follows:

        - Damp or Wet Locations: NEMA 250, Type 4, stainless steel.

        - Indoor Dusty Locations: NEMA 12

        - Damp or Wet and Corrosive Locations: NEMA 250, Type 4X, stainless steel.

        - Hazardous Locations: NEMA 250, Type 7.

  - INSTALLATION

    - Install raceways and boxes as indicated, according to manufacturer’s written instructions. Use raceway fittings compatible with raceways and suitable for use and location.

    - Seal all conduits which pass through the building roof, through outside walls of the building above or below grade, and through floor slabs on grade. Seal on the end inside the building using a pliable duct-sealing mastic, non-hardening compound packed around the wire in the conduit. Compound shall be a type specially designed for such service on electrical wiring systems, shall be non-combustible and shall have the approval of the code-enforcing agency.

    - Install raceways to preserve the fire resistance rating of partitions and other elements using materials and methods as specified in Section 07 84 00 - Firestopping. Apply firestopping to cable and raceway penetrations of fire-rated floor and wall assemblies as required to reestablish the original fire-resistance rating.

    - Clip type conduit fasteners are not allowed. All fasteners and clamps for conduit and raceway support shall be bolted mechanical hardware type.

    - Raceways:

      - Minimum Raceway Size:

        - 1/2” trade size for end use devices and communications.

        - 3/4” trade size for homeruns, conduit embedded in slabs, and for outdoor applications.

      - Cut conduit square using a saw or pipe cutter and ream to remove burrs.

      - Use hydraulic one-shot conduit bender or factory elbows for bends in conduit larger than 2-inch size.

      - Conceal conduit and EMT, unless otherwise indicated, within finished walls, ceilings, and floors.

        - Run concealed raceways, with a minimum of bends, in the shortest practical distance considering the type of building construction and obstructions, unless otherwise indicated.

      - Conveyor areas should be considered a NEMA 12 installation because of dust. Conduit shall be RMC up to 10’ AFF or within a 10’ radius of conveyors.

        - Device and pull boxes within 10’ of conveyors shall be gasketed.

      - Conduits shall not be supported from ducts, pipes or other systems foreign to the electrical installation. The entire electrical installation shall be kept independent from any other trade.

      - Provide separate conduits for 480/277V, 208/120V and low voltage and controls cabling.

      - Planning: the layout of all raceways shall be carefully planned by the Contractor to ensure an installation which is neatly done and workmanlike. Any Work showing improper care in planning will be ordered removed by the Engineer, and shall be replaced in a neat and proper manner, without any additional cost to the Port.

      - Run concealed raceways with a minimum of bends, in the shortest practical distance considering type of building construction and obstructions.  Install no more than the equivalent of four 90-degree bends in any conduit run except for control wiring conduits, for which fewer bends are allowed. Support within 12 inches of changes in direction.

      - Expansion-Joints:

        - Provide Liquid tight flex conduit at expansion joints with sufficient slack to accommodate seismic movement, unless Structural Engineer requires expansion joint fitting. Wrap flex conduit with ground wire, connected to steel fittings at either end of flex.

      - Flexible Conduit: Comply with NEMA RV 3. Use a maximum of 72 inches of flexible conduit for recessed and semi-recessed luminaires, equipment subject to vibration, noise transmission, or movement; and for transformers and motors. Flexible conduit is also allowed at expansion joints. Any other use of flexible conduit must be approved by the Engineer.  Install a separate external ground connector across flexible connections. See Section 26 05 26 – Grounding.

        - Use LFMC in damp or wet locations subject to severe physical damage.

      - Install raceways parallel and perpendicular to structure and at proper elevations. Group multiple conduit runs and neatly rack and support from the structure. Provide adequate headroom.

        - Maintain 6-inches minimum clearance between raceways and mechanical piping and 12-inches minimum to heat sources such as flues, steam piping and heating appliances. Install horizontal raceway runs above water and steam piping.

        - Give right of way to raceways and piping systems installed at a required slope.

        - Keep electrical conduits free from contact with other dissimilar metals.

Delete paragraph below if no high-frequency installation.

      - Install nonferrous conduit or tubing for circuits operating above 60 Hz. Where aluminum raceways are installed for such circuits and pass through concrete, install in a nonmetallic sleeve. Do not install aluminum conduits embedded in or in contact with concrete.

      - Raceways Embedded in Slabs: Install in middle third of slab thickness where practical, and leave at least 1-inch concrete cover.

        - Secure raceways to reinforcing rods to prevent sagging or shifting during concrete placement.

        - Space raceways laterally to prevent voids in concrete.

        - Run conduit larger than 1-inch trade size parallel to or at right angles to main reinforcement.

        - Transition from nonmetallic tubing to Schedule 80 nonmetallic conduit or rigid steel conduit at all bends and before rising above floor.

      - Stub-up Connections: Extend conduits through concrete floor for connection to freestanding equipment.

        - Protect stub-ups from damage where conduits rise through floor slabs. Arrange so curved portion of bends is not visible above the finished slab.

        - Install with an adjustable top or coupling threaded inside for plugs set flush with the finished floor.

        - Extend conductors to equipment with rigid steel conduit; FMC may be used 6 inches above the floor.

        - Install screwdriver-operated, threaded flush plugs flush with floor for future equipment connections.

      - Flexible Connections:

        - Use a maximum of 6 feet of flexible conduit for recessed and semi-recessed lighting fixtures. Use a maximum of 18” for equipment subject to vibration, noise transmission or movement, and for all motors. Use liquidtight flexible conduit in wet or damp locations.

        - Install combination deflection/expansion fittings, including bonding jumper, where raceway system crosses building seismic, control or expansion joints.

      - Sleeves: Install for cable and raceway penetrations of concrete slabs and walls, except where core-drilled holes are used. Install for cable and raceway penetrations of masonry and fire-rated gypsum walls and of all other fire-rated floor and wall assemblies. Install sleeves during erection of concrete and masonry walls.

      - Avoid moisture traps. Provide junction box with drain fitting at low points in conduit system.

      - Install raceway sealing fittings according to manufacturer’s written instructions. Locate fittings at suitable, approved, and accessible locations and fill them with UL-listed sealing compound. For concealed raceways, install each fitting in a flush steel box with a blank cover plate having a finish similar to that of adjacent plates or surfaces. Install raceway sealing fittings at the following points:

        - Where conduits pass from warm to cold locations, such as the boundaries of refrigerated spaces.

        - Where otherwise required by NFPA 70 (NEC).

      - Terminations: Where raceways are terminated with locknuts and bushings, align raceways to enter squarely and install locknuts with dished part against the box.

        - Where raceways are terminated with threaded hubs, screw raceways or fittings tightly into the hub so the end bears against the wire protection shoulder. Where chase nipples are used, align raceways so the coupling is square to the box and tighten the chase nipple so no threads are exposed.

      - Use temporary closures to prevent foreign matter from entering raceways.

      - Complete raceway installation before starting conductor installation.

      - In public areas, exposed raceways shall be painted to match surroundings. In other exposed areas of the Terminal, raceways may be painted to match existing finishes.

      - Install pull-ropes in empty raceways except at sleeves and nipples. Use #14 AWG zinc-coated steel or monofilament plastic line with not less than 200-lb tensile strength. Leave at least 12 inches of slack at each end of the pull wire.

      - Surface Conduits: Install a separate, green, ground conductor in conduits from junction box supplying the conduits to receptacle or fixture ground terminals.

        - Select each surface raceway outlet box, to which a lighting fixture is attached, of sufficient diameter to provide a seat for the fixture canopy.

        - Where a surface raceway is used to supply a fluorescent lighting fixture having central-stem suspension with a backplate and a canopy (with or without extension ring), no separate outlet box is required.

        - Provide surface metal raceway outlet box, and the backplate and canopy, at the feed-in location of each fluorescent lighting fixture having end-stem suspension.

        - Where a surface metal raceway extension is made from an existing outlet box on which a lighting fixture is installed, no additional surface-mounted outlet box is required. Provide a backplate slightly smaller than the fixture canopy.

    - Outlet Box Installation:

      - Provide cast outlet boxes in exterior or wet locations.

      - Provide recessed outlet boxes in finished areas.

        - Do not install boxes back-to-back in walls.

        - Provide 6-inch minimum separation; 24-inch in acoustic rated walls.

      - Sectional boxes are not permitted.

      - Provide knockout closures for unused openings.

      - Where receptacle boxes and telecom devices are adjacent to one another, install receptacles not closer than 6” to and not greater than 12” from telecom device.

      - Support boxes independently of raceway. Mount device boxes to wall studs using blocking material behind the box to insure that the box will remain square to the finished wall surface.

      - Outlet and device boxes mounted in masonry walls shall be set at the bottom or top of a masonry unit course.

      - Use multiple-gang boxes where more than one device is mounted together; do not use sectional boxes.

      - Support boxes of three gangs or more from more than one side by spanning two framing members or mounting on brackets specifically designed for the purpose.

      - Provide cast outlet boxes in exterior or wet location. Conduit shall not enter the top or sides of exterior wall outlet boxes. Conduit shall enter bottom only.

      - Coordinate location and mounting height of outlets mounted above counters, benches, and backsplashes.

      - Mount outlets at the following heights above finished floor, unless otherwise noted on drawings:

        - Wall Switches:	48”

        - Convenience Outlets – Utility areas:	 48”

        - Convenience Outlets – other areas: 18”

        - Above Counter Outlets: 48” or 6” above counter or backsplash

        - Telephone outlets : 18”

        - Wall phone outlets: 54”

        - Thermostats: 60”

    - Pull and Junction Box Installation:

      - Provide as required to facilitate installation of the Work or as required by NFPA 70 (NEC).

      - Locate so that covers are accessible at all times.

      - Support boxes independently of raceway. Fasten junction and pull boxes to or support from building structure.

    - Floor Box Installation:

      - Set floor boxes level and adjust to finished floor surface.

      - Use cast iron floor boxes for installations in slab on grade.

  - GROUNDING

    - Provide grounding connections for raceway, boxes, and components as specified in Section 26 05 26 - Grounding and as required by NFPA 70 (NEC).

  - SUPPORT

    - Support raceways as specified in Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

  - IDENTIFICATION

    - Provide labels for raceway, boxes, and components as specified in Section 26 05 53 - Electrical Identification.

    - Raceways for medium-voltage circuits:

      - Apply self-adhesive labels on raceways leaving equipment and at 25-foot intervals indicating system voltage. Use 1-1/4” minimum black letters on yellow background.

      - Label raceways entering concealed locations from exposed locations as to the destination via the concealed area.

      - Apply self-adhesive labels on exterior door or cover of enclosures indicating system voltage. Use 1-1/4” minimum black letters on orange background.

    - Raceways for low-voltage circuits:

      - System Identification Color-Coding Bands for Raceways: Each color-coding band shall completely encircle cable or conduit. Place adjacent bands of two-color markings in contact, side by side. Locate bands at changes in direction, at penetrations of walls and floors, at 50-foot (15-m) maximum intervals in straight runs, and at 25-foot (7.6-m) maximum intervals in congested areas.

      - 208/120V	Blue

      - 480/277V	Yellow

      - Controls	Black

      - Accessible Raceways, More Than 600 V: Self-adhesive vinyl labels. Install labels at all conduit penetrations and along length of exposed conduit run at 25 foot maximum intervals.

      - Accessible Raceways within Buildings: Identify the covers of each junction and pull box of the following systems with self-adhesive vinyl labels with the wiring system legend and system voltage.

      - Provide labels on all raceways, junction and pull boxes indicating panel designation and circuit number for all circuits in raceway or box, and conduit destination.

      - Conduit Label Example: B2-P4-23G-1/1,3,5, B-2601-9.

      - Provide labels at all locations where conduit penetrates walls, floors and ceilings, on both sides of penetration.

      - Provide labels at all ends or breaks in conduit runs such as electrical rooms, junction boxes, pull boxes, cabinets, maintenance holes, fire penetrations, etc.

      - Provide labels on each conduit entering junction or pull box within 12” of junction or pull box.

      - Provide labels at 25 foot maximum intervals along conduit runs.

      - Provide labels on all junction and pullboxes, including in accessible ceiling spaces and exposed in unfinished areas. Refer to specification sections for identification requirements for systems contained within.

      - Install labels parallel to equipment lines.

      - Labels in unfinished locations, including in accessible ceiling spaces and exposed unfinished areas shall be plain colored vinyl adhesive tape, minimum ½ inch high, handwritten in black indelible ink.

      - Labels in finished locations shall be adhesive-backed plastic machine printed labels, minimum 3/8 inch high, white with black letters.

      - Lettering shall be a minimum of ¼” high.

      - In finished locations, provide labels on inside of junction or pull box cover.

      - Provide red lettering when served by an emergency source.

      - Label power junction and pull boxes with power source and circuit numbers.

      - Label raceways entering concealed locations from exposed locations as to the destination via the concealed area.

  - PROTECTION

    - Provide final protection and maintain conditions, in a manner acceptable to manufacturer and installer that ensure coatings and finishes are without damage or deterioration at the time of Substantial Completion.

      - Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

      - Repair damage to PVC or paint finishes with matching touchup coating recommended by manufacturer.

  - CLEANING

    - On completion of installation, including outlet fittings and devices, inspect exposed finish. Remove burrs, dirt, and construction debris and repair damaged finish, including chips, scratches, and abrasions.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions