READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Medium-Voltage Transformers” Work is shown in the Contract Documents. This section includes requirements for design, fabrication, testing and delivery of distribution and power transformers with medium-voltage primaries, including liquid-filled padmounted, liquid-filled secondary substation and dry-type secondary substation transformers.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - ANSI C37.47 - Specifications for Distribution Fuse Disconnecting Switches, Fuse Supports, and Current-Limiting Fuses

    - ANSI C57.12.28 - Switchgear and Transformers - Pad-Mounted Equipment - Enclosure Integrity

    - ANSI C57.12.55 - Conformance Standard for Dry-Type Transformers in Unit Installations, Including Unit Substations

    - IEEE C57.12.00 - General Requirements for Liquid-Immersed Distribution, Power, and Regulating Transformers

    - IEEE C57.12.90 - Test Code for Liquid-Immersed Distribution Power, and Regulating Transformers and Guide for Short-Circuit Testing of Distribution and Power Transformers

    - IEEE C57.12.91 - Test Code for Dry-Type Distribution and Power Transformers

    - IEEE C57.94 - Recommended Practice for Installation, Application, Operation, and Maintenance of Dry-Type General Purpose Distribution and Power Transformers

    - IEEE C57.106 - Guide for Acceptance and Maintenance of Insulating Oil in Equipment

    - IEEE C57.111 - Guide for Acceptance of Silicone Insulating Fluid and Its Maintenance in Transformers

    - IEEE C57.121 - Guide for Acceptance and Maintenance of Less Flammable Hydrocarbon Fluid in Transformers

    - IEEE 386 - Separable Insulated Connector Systems for Power Distribution Systems Above 600 V

    - NEMA AB 1 - (National Electrical Manufacturers Association)  Molded Case Circuit Breakers and Molded Case Switches

    - NEMA 260 (National Electrical Manufacturers Association) - Safety Labels for Padmounted Switchgear and Transformers Sited in Public Areas

    - NETA ATS - Acceptance Testing Specifications for Electrical Power Distribution Equipment (International Electrical Testing Association)

    - NFPA 70 (National Fire Protection Association) - National Electrical Code

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: Include data on features, components, ratings, and performance for each type of transformer specified.

        - Include dimensioned plans, sections, and front elevation views showing all devices.

        - Transformer outline drawing with actual transformer dimensions and weights with and without oil.

        - Show minimum clearances and installed devices and features.

        - Provide component list.

        - Show conduit entry and exit locations.

        - Install nameplate diagram per ANSI requirements.

      - Provide transformer ratings, including percentage impedance.

      - Wiring Diagrams: Detail wiring and identify terminals for tap changing and connecting field-installed wiring.

      - Product Certificates: Signed by manufacturers of transformers certifying that the products furnished comply with requirements.

      - Manufacturer Seismic Qualification Certification: Submit certification that transformer assembly and components will withstand seismic forces defined in Section 26 05 48 - Seismic Controls for Electrical and Communication Work. Include the following:

        - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

        - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

        - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Delete below if factory test reports are not required. Delete “design and” if reports of routine tests suffice.

      - Factory Test Reports: Certified copies of manufacturer’s design and routine factory tests required by referenced standards.

Delete below unless equipment sound-level ratings lower than NEMA standards are specified.

      - Sound-Level Test Reports: Certified copies of manufacturer’s sound-level tests applicable to equipment for this Project.

      - Field Test Reports: Indicate and interpret test results for tests specified in Part 3.

      - Maintenance Data: For transformers to include in the maintenance manuals specified in Division 1 General Requirements.

  - QUALITY ASSURANCE

    - Listing and Labeling: Provide transformers that are Listed and Labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to the Authority Having Jurisdiction, and marked for intended use for the location and environment in which they are installed.

    - Comply with IEEE C2.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

    - Testing Agency Qualifications: Testing agency meeting OSHA criteria for accreditation of testing laboratories, Title 29, Part 1907 or a member company of the InterNational Electrical Testing Association and that is acceptable to Authority Having Jurisdiction.

      - Testing Agency’s Field Supervisor: Person currently certified by the InterNational Electrical Testing Association to supervise on-site testing specified in Section 26 08 00 - Acceptance Testing.

  - DELIVERY, STORAGE, AND HANDLING

    - Temporary Heating: For indoor, dry-type transformers, apply temporary heat according to manufacturer’s written instructions within the enclosure of each ventilated-type unit throughout periods during which equipment is not energized and is not in a space that is continuously under normal control of temperature and humidity.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Padmounted transformers, furnish three spare primary fuse assemblies, complete with all fuses, fuse links, cartridges and holders, housed in a separate pocket in the primary compartment door with phenolic label indicating “Spare Fuses.”

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - ABB Power T & D Co., Inc.

      - GEC Alsthom T&D Balteau.

      - GE Electrical Distribution & Control.

      - Or Approved Equal.

  - TRANSFORMERS, GENERAL

Revise paragraph below to show type of supply system to be accommodated by transformers on this Project. Dual-voltage rated medium-voltage transformers shall only be used where the existing primary feed is 4160V; otherwise, all new medium-voltage transformers shall be single-voltage rated at 12.47 kV only. The Port is in the process of converting all 4160V primary to 12.47 kV where possible and necessary.

    - Windings: 2-winding type, designed for operation with [12,470V] [12,470/4160V Dual Voltage - padmounts only] [4160V] high-voltage connected to a 3-phase, 4-wire, 60-Hz, grounded neutral distribution system.

    - Winding Material: Copper insulation shall be Class H

    - Busses and Terminals: Copper.

Select first choice below unless transformer(s) are required to be low-sound-level units.

    - Sound Level Standards: [Sound level standards as defined in NEMA and ANSI] [Low-sound level rating of 3 dB minimum less than NEMA TR 1 standard sound levels for transformer type and rating - in noise sensitive areas].

Since all liquid-filled substation transformers and dry-type transformers require fan cooling, include paragraph below. Coordinate with Drawings for fan-power source.

    - Forced-Air Cooling Provisions: Cooling fans, temperature-sensing devices, and controls; complete with housings, mounting devices, conduit, and wiring.

      - Cooling-Fan Operation: Automatically and sequentially controlled by temperature-sensing devices.

      - Manually Operable Switch: Connected in parallel with automatic-control contacts.

      - Enclosure for Controls: Cabinets mounted on side of transformer at a height not more than 60 inches above base.

      - Cooling Fans: Propeller type, with aluminum blades and direct-drive, totally enclosed, fan-cooled motors.

      - Motor Circuits: Individually fused or thermally protected.

      - Fans: OSHA blade guards.

      - Fan Control: Thermally operated, windings’ temperature-sensing devices.

Remove below paragraph requiring differential relay protection for Airport Projects.

    - In general, transformers sized at 3750 kVA and larger shall be fed from a dedicated feeder. Where possible, these transformers shall be provided with suitable differential protection (ANSI device 87) scheme, whereby activation of the 87 relay shall trip and lockout the upstream drawout circuit breaker or load interrupter switch.

    - All transformers above 150 kVA shall be furnished with two each full capacity taps above and below normal. four

  - DRY-TYPE TRANSFORMERS

    - Comply with NEMA ST 20, IEEE C.57.12.01, and IEEE C57.94, and list and label as complying with UL 1562.

If all transformers have same enclosure, select from 3 paragraphs below. If enclosures vary, delete all and show on Drawings.

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Sola Hevi-Duty

      - General Electric Co

      - ASEA Brown Boveri; Division of ABB.

      - ABB Power T & D Co., Inc.

      - Cutler-Hammer; Division of Eaton.

      - GE Electrical Distribution & Control.

      - EATON Square D Co.

      - Or Approved Equal.

    - Ratings:

Although higher rated transformers are available, recommended maximum kVA for 3-phase transformers is 1500 kVA at 480Y/277V and 500 kVA at 208Y/120V. Higher ratings require F&I approval.

      - kVA Rating: 75 kVA through 2500 kVA.

Use value indicated on the drawings or, if none indicated, manufacturer’s standard.

      - Impedance: Varies with kVA rating (2.20% to 5.75%).

      - Nominal Primary Voltage: [12.47 Delta] [4.16/12.47 kV Dual Voltage, Delta] [4.16 kV Delta].

      - Nominal Secondary Voltage: [480Y/277 Volts, 3-phase, 4-wire] [208Y/120 Volts, 3-phase, 4-wire] [120/240 Volts, 3-phase, 3-wire].13W.

      - MV BIL: [95 kV at 12,470V] [60 kV at 4160V].

      - LV BIL: 10 kV

Revise paragraph below if other than NEMA standard taps are required.

    - Full-Capacity Voltage Taps: Four 2-1/2% taps; 2 above and 2 below rated full voltage.

Select one of the 3 choices in paragraph below. Highlighted choice is preferred for indoor applications.

    - Enclosure: [Indoor, ventilated] [Outdoor, ventilated, raintight, NEMA 250, Type 3R] [Totally enclosed, non-ventilated].

    - Cooling System: Comply with IEEE C57.12.01, equipped for forced-air cooling; Class AA/FFA above 500 kVA.

    - Insulation Class: 185°C insulation system.

Dry-type transformers with an insulation temperature rise of 150°C are not acceptable. Dry-type transformers with an insulation temperature rise of 80°C are acceptable with F & I approval only.

    - Insulation Temperature Rise: 115°C maximum rise above 40°C.

    - Include the following Accessories:

Delete items below if not required.

      - External Medium-Voltage Surge Arresters: Distribution class, low flashover, metal oxide varistor type complying with NEMA LA 1; factory installed and connected to high-voltage terminals.

      - External Low-Voltage Surge Arresters: Metal oxide varistor type complying with NEMA LA 1; factory installed and connected to low-voltage terminals.

      - High-Voltage Terminal Compartment: Full-height steel compartment to match transformer.

      - Low-Voltage Terminal Compartment: Full-height steel compartment to match transformer.

If retaining below, coordinate with Drawings, provide external power and signal connections, and specify remote indicating device or alarm annunciator.

      - High-Temperature Alarm: A sensor at the transformer with local audible with manual switch override and visual alarm and contacts for remote alarm. Provide LED display with current temperature display and highest temp hold and reset functions.

  - LIQUID FILLED PAD-MOUNTED TRANSFORMERS

Select from 2 paragraphs below. First includes pad-mounted transformers with livefront high-voltage bushing. Second includes units equipped for deadfront, separable, insulated, high-voltage, load-break cable connectors.

Verify compliance with NEC and environmental regulations that may require containment of insulating liquid leaks or spills.

    - Acceptable Manufacturers:

      - GEC Alsthom T&D Balteau

      - General Electric Co.

      - ASEA Brown Boveri; Division of ABB.

      - Or Approved Equal.

    - Description: Comply with IEEE C57.12.22 and ANSI C57.12.28 for livefront applications.

    - Description: Comply with IEEE C57.12.26 and ANSI C57.12.28 for deadfront applications.

Select from 3 paragraphs below to specify insulating liquid.  Liquid must be UL listed as complying with NFPA 70 requirements for fire point of not less than 300 deg C when tested according to ASTM D 92.

    - Insulating Liquid: Mineral oil, complying with ASTM D 3487, Type II, tested according to ASTM D 117.

    - Insulating Liquid: High-molecular weight, mineral-oil based, and listed as less-flammable type.

Where arcing contacts, such as load-break switches, are immersed, use special caution applying silicone liquid in paragraph below.

    - Insulating Liquid: Silicone, listed as less-flammable type. Liquid can extinguish small arcing and has a minimum fire point, thermal conductivity and dielectric strength as noted in ASTM D 877. Insulating Liquid: mineral oil; silicon; hydro-carbon less flammable/high fire point liquid.

      - Rated Temperature Rise: 65°C maximum rise above 40°C.

      - BIL: Standard value for nominal primary equipment voltage per applicable IEEE standard.

    - Ratings:

Although higher rated transformers are available, [recommended maximum kVA for 3-phase transformers is 1500 kVA at 480Y/277V and 500 kVA at 208Y/120V. Higher ratings require F & I approval]. [Recommended maximum kVA for 3-phase transformers is 2500 kVA at 480Y/277V and 750 kVA at 208Y/120V. Higher ratings require approval.]

      - kVA Rating: 75 kVA through 2500 kVA at 65°C.

      - Impedance: Varies with kVA rating (2.20% to 5.75%).

      - Nominal Primary Voltage: [12.47 Delta] [4.16/12.47 kV Dual Voltage, Delta] [4.16 kV Delta].

      - Nominal Secondary Voltage: [4,160Y/2400 Volts, 3-phase, 4-wire] [480Y/277 Volts, 3-phase, 4-wire] [208Y/120 Volts, 3-phase, 4-wire] [120/240 Volts, 3-phase, 3-wire].13W

      - MV BIL: [95 kV at 12,470V] [60 kV at 4160V].

      - LV BIL: 30 kV.

    - Construction: Compartmental type, self-cooled and tamper resistant for mounting on a pad, designed to restrict entry of water into the compartments.

    - Full-Capacity Voltage Taps: Four 2-1/2% taps; 2 above and 2 below rated high voltage, with externally operable tap changer for de-energized use and with a position indicator and padlock hasp.

    - Features:

      - Configuration: Full-height, bolt-on, high- and low-voltage cable terminating compartments side-by-side separated with a rigid metal barrier, with the high-voltage compartment on the left. Each compartment shall have separate doors.

      - Locking and Access: The low-voltage compartment door equipped with a steel rod handle with provisions for padlocking. Both compartment doors must be capable of being secured with a single padlock. Doors so arranged that accessibility to the high-voltage compartment can only be gained after opening the low-voltage compartment door and a captive screw released.

      - Hinged doors: Provide stainless-steel hinges equipped with captive hold-open devices.

      - Lifting: Lifting attachments to carry the full weight of the transformer in accordance with ANSI.

      - Jacking and Rolling: Provide removable door sill on compartments to permit rolling or skidding of unit into place over conduit studs in pad.

      - Grounding: Provide grounding in both the high-voltage and low-voltage compartments.

      - Secondary Bushings: Low-voltage bushings shall be tin-plated spade type arranged for vertical takeoff of outgoing cables.

      - Finish: Painted ANSI 61 olive-green color, 3-mil paint thickness required. All hardware corrosion resistant stainless steel. Underside of enclosure including channels, skids, beams and plates undercoated.

Select 1 of 3 paragraphs below to suit transformer arrangement. Consider need for visible verification of switch position. Coordinate switch ratings with transformer rating, system fault currents, and BIL for associated equipment.

    - High-Voltage Switching: Provide a separate pad-mounted vacuum interrupter switch per Section 26 13 19 - Medium-Voltage Pad-Mounted Vacuum Interrupter Switchgear. Physically arrange switch such that the line side of the switch is at the top and the load side is at the bottom. Need for visible verification of switch position and a 3-phase, gang-operated, load-break switch, oil-immersed in transformer tank, with hook-stick-operated handle in the primary compartment, arranged for radial feed, for transformer energization and de-energization.

    - High-Voltage Switching: Arranged for radial feed with 3-phase, 2-position, gang-operated, load-break switches that are oil immersed in transformer tank with hook-stick operating handle in primary compartment.

Loop-feed arrangement below requires F & I approval and may only be used for radial feed to provide an extra set of terminals for deadfront, insulated, load-break, connector-type surge arresters.

    - High-Voltage Switching: Arranged for loop feed with 3-phase, 4-position, gang-operated load-break switch that is oil immersed in transformer tank with hook-stick operating handle in primary compartment.

    - Primary Fusing by Manufacturer:

      - Radial Feed Primary Connections: Transformer primary connections shall be dead-front, non-loadbreak, separable insulated high-voltage connector bushings OR Transformer primary connections shall be live-front with NEMA spades and terminals suitable for cable sizes.

      - High Voltage Terminations and Equipment:  [Dead-front with universal-type bushing well inserts.  Include the following:  bushing well inserts, lightning arrestors, parking stands, portable insulated bushings.] OR [live front, with externally clamped porcelain bushings and cable connectors suitable for terminating primary cable.]

      - Internal Isolation Link: Each transformer shall be supplied with a coordinated internal isolation link in series with bayonet type expulsion/ELSP fuses for protection during transformer switching and refusing operations.

      - Overload and Short Circuit Protection:

Select from two paragraphs below. The first paragraph should be the typical selection unless approved by F & I.

        - Provide under oil current-limiting fuses in series with load-sensing bayonet expulsion fuses.

        - Provide full-range current limiting fuses in load-break dry well canisters in series with load-sensing bayonet expulsion fuses.

    - Radial Feed Primary Connections:

Select from 2 paragraphs below. The first paragraph should be the typical selection unless approved by F & I.

      - Transformer primary connections shall be deadfront, non-load-break, separable insulated high-voltage connector bushings.

      - Transformer primary connections shall be livefront with NEMA spades and terminals suitable for cable sizes.

Select from 2 paragraphs below. The first paragraph should be the typical selection unless approved by F & I.

    - High-Voltage Terminations and Equipment: Deadfront with universal-type bushing wells inserts. Include the following:

      - Bushing-Well Inserts: One for each high-voltage bushing well.

      - Parking Stands: One for each high-voltage bushing well.

      - Portable Insulated Bushings: Arranged for parking insulated, high-voltage, load-break cable terminators; one for each primary feeder conductor terminating at transformer.

      - Surge Arresters: Distribution class, one for each primary phase. Comply with NEMA LA 1.

Select from 2 paragraphs below. The first paragraph should be the typical selection unless approved by F & I.

        - External distribution-type [direct connected to bushings] [piggyback behind load-break elbows].

        - Internal lightning metal oxide distribution type arresters. Support from tank wall within high-voltage compartment.

    - High-Voltage Terminations and Equipment: Comply with IEEE 386. Livefront with externally clamped porcelain bushings and cable connectors suitable for terminating primary cable.

    - Accessories (500 kVA and below):

      - Lightning Arrestors: [External distribution-type direct connected to bushings] OR, [piggy-back behind loadbreak elbows] OR [Internal lightning metal oxide distribution type arresters].

      - Tap-Changer Control: [150-ampere] [300-ampere] tap-changer.

      - Secondary Feeder Breaker: [Specify maximum rating of molded-case breaker for channel mounting in the low-voltage compartment, if required].

      - Low-Voltage Busway: [Specify if busway entrance through secondary compartment cover is required].

      - Metering: [Specify metering requirements if required].

Delete items below if not required. Coordinate with Drawings.

    - Accessories (750 kVA and above):

      - One-inch globe type drain valve with sampling device.

      - Dial-type thermometer.

      - Liquid-level gauge.

      - Pressure-vacuum gauge.

      - Pressure-relief device: Self-sealing with indicator.

      - Mounting provisions for low-voltage current transformers.

      - Mounting provisions for low-voltage potential transformers.

      - Alarm contacts for above gages

      - Nameplates required per NEC and supplemental Port required nameplates per attached Interior and Exterior Nameplate Schedules.

If retaining either item below, provide detailed requirements here or on Drawings.

      - Busway terminal connection at low-voltage compartment.

      - Alarm contacts for gages and thermometer.

  - LIQUID-FILLED UNIT SUBSTATION TRANSFORMERS

Use this Article for substation-type transformers used independently of unit substations. When applying liquid-filled transformers, verify compliance with NEC and environmental regulations that may require containment of insulating liquid leaks or spills.

    - Comply with IEEE C57.12.00 and ANSI C57.12.13.

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - GEC Alsthom T&D Balteau

      - ASEA Brown Boveri; Division of ABB.

      - EATON

      - Square D. Co.; Division of EATON

      - Cooper; Division of EATON

      - ABB Power T & D Co., Inc.

      - Cutler-Hammer; Division of EATON

      - GE Electrical Distribution & Control.

      - Or Approved Equal.

Select from 3 paragraphs below to specify insulating liquid. Mineral oil is the preferred choice.

    - Insulating Liquid: Mineral oil, complying with ASTM D 3487, Type II, tested according to ASTM D 117.

    - Insulating Liquid: High-molecular-weight, mineral oil based, and listed as less-flammable type. Listing shall be for application equivalent to that required for this Project.

Where arcing contacts, such as load-break switches, are immersed, use special caution applying silicone liquid in paragraph below.

    - Insulating Liquid: Silicone, listed as less-flammable type. Liquid can extinguish small arcing and has a minimum fire point, thermal conductivity and dielectric strength as noted in ASTM D 877.

      - Rated Temperature Rise: 65°C maximum rise above 40°C.

      - BIL: Standard value for nominal primary equipment voltage per applicable IEEE standard.

    - Ratings:

Although higher rated transformers are available, recommended maximum kVA for 3-phase transformers is 1500 kVA at 480Y/277V and 500 kVA at 208Y/120V. F & IRecommended maximum kVA for 3-phase transformers is 2000 kVA at 480Y/277V and 750 kVA at 208Y/120V. Higher ratings require F&I approval.

      - kVA Rating: 500 kVA through 2500 kVA at 65°C insulation temperature rise.

Use value indicated on the drawings or, if none indicated, manufacturer’s standard.

      - Impedance: Varies with kVA rating (2.20% to 5.75%).

      - Nominal Primary Voltage: [12.47 Delta] [4.16 kV Delta].

      - Nominal Secondary Voltage: [4,160Y/2400 Volts, 3-phase, 4-wire] [480Y/277 Volts, 3-phase, 4-wire] [208Y/120 Volts, 3-phase, 4-wire] [120/240 Volts, 1-phase, 3-wire].

      - MV BIL: [95 kV at 12,470V] [60 kV at 4160V].

      - LV BIL: 30 kV

Revise paragraph below if other than NEMA standard taps are required. Coordinate with schedule.

    - Full-Capacity Voltage Taps: Four 2-1/2% taps; 2 above and 2 below rated high voltage, with externally operable tap changer for de-energized use and with a position indicator and padlock hasp.

    - Cooling System: Comply with IEEE C57.12.00, equipped for forced-air cooling; Class OA/FFA above 1500 kVA.

    - Bushing Mounting Arrangement: High- and low-voltage bushings mounted on opposite sides of transformer.

Verify availability of specific accessories with manufacturers. Delete items not required.

    - Accessories:

      - Lightning Arresters: Utility grade Distribution-type, connected to high-voltage terminals

      - Surge Arresters: Distribution-type, connected to high-voltage terminals.

      - Surge Arresters: Low-voltage type, connected to low-voltage terminals.

      - Medium-Voltage Terminal Compartment: Full-height steel for side-mounted terminals.

      - Low-Voltage Terminal Compartment: Full-height steel compartment.

      - One-inch globe type drain valve with sampling device.

      - Dial-type thermometer.

      - Liquid-level gauge.

      - Pressure-vacuum gauge.

      - Pressure-Relief Device: Self-sealing with an indicator.

      - Mounting provisions for low-voltage current transformers, if required.

      - Mounting provisions for low-voltage potential transformers, if required.

If retaining next two paragraphs, provide detailed requirements here or on Drawings.

      - Busway terminal connection at low-voltage compartment.

      - Alarm contacts for gages.

      - Nameplates as required by Port and Authority Having Jurisdiction.

  - FINISHES

    - Enclosure Coating System for Outdoor Units: Comply with ANSI C57.12.28 regardless of transformer type.

  - SOURCE QUALITY CONTROL

    - Factory Tests: Design and routine tests comply with referenced standards.

Delete below unless sound level is critical and low-sound-level units are required.

    - Factory Sound-Level Tests: Conduct sound-level tests on equipment for this Project if specified sound levels are below standard ratings.

- EXECUTION

  - INSTALLATION

    - Comply with IEEE C2.

    - Install transformers on concrete bases.

      - Anchor transformers to concrete bases according to manufacturer's written instructions, seismic codes at Project, and requirements in Section 20 05 29 - Hangers and Supports.

      - Construct concrete bases of dimensions indicated, but not less than 4 inches larger in both directions than supported unit and 3.5 inches high.

      - Use 3000-psi, 28-day compressive-strength concrete and reinforcement.

      - Install dowel rods to connect concrete bases to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch centers around full perimeter of base.

      - Install epoxy-coated anchor bolts, for supported equipment, that extend through concrete base and anchor into structural concrete floor.

      - Place and secure anchorage devices. Use supported equipment manufacturer's setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

      - Tack-weld or bolt transformers to channel-iron sills embedded in concrete bases. Install sills level and grout flush with floor or base.

    - Bring transformer to room temperature or a minimum of 65°F for a period of 24 hours prior to energizing. Temperature as measured at transformer hot spot.

    - Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A and UL 486B.

      - Mark lugs after torquing with red paint such that paint will be visibly disturbed if lugs are disturbed.

  - IDENTIFICATION

    - Provide labels for enclosures and components as specified in Section 26 05 53 - Electrical Identification.

    - General: Provide label on the inside door of all pad-mounted liquid-filled transformers, and at the exterior of all medium-voltage transformers located indoors.

    - Exterior Label: Provide the following information stenciled in yellow paint, with 2” high letters on all exterior transformers:

      - Port of Seattle Assigned Equipment Number.

      - Transformer kVA Size.

      - Primary/Secondary Voltage.

Delete Paragraph below except for pad-mounted transformers.

    - Interior Labels: Provide engraved plastic laminate labels, white letters on black background, 1” high minimum for the following:

      - Both sets of high-voltage bushing wells (H1A, H2A, H3A and H1B, H2B, H3B).

      - Secondary bushings (X0, X1, X2, X3).

      - Liquid level gauge (750 kVA and above).

      - Vacuum/pressure gauge (750 kVA and above).

      - Dial type thermometer (750 kVA and above).

      - One-inch drain valve and sampler (750 kVA and above).

    - Provide warning and caution signs where indicated or required by the Authority Having Jurisdiction.

  - FIELD QUALITY CONTROL

    - Manufacturer’s Field Services: Engage a qualified factory-trained representative to assist in installation and start-up. Manufacturer’s representative shall provide technical direction and assistance to Contractor in general assembly of equipment, connections and adjustments, and testing.

    - Seismic Anchoring: Install transformers on concrete base and meet seismic anchoring and bracing requirements. Refer to Section 03 30 00 - Cast-in-Place Concrete and Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

    - Grounding: Comply with Section 26 05 26 - Grounding for materials and installation requirements.

Coordinate paragraph below with Drawings.

      - Separately Derived Systems: Make grounding connections to grounding electrodes and bonding connections to metallic piping to comply with NFPA 70 and Section 26 05 26 - Grounding.

  - FIELD TESTING

    - Installing Contractor Inspection and Testing: Prior to acceptance testing by an independent testing agency, the installing Contractor shall perform the following:

      - Inspect accessible components for cleanliness, mechanical and electrical integrity, and damage or deterioration. Verify that temporary shipping bracing has been removed. For dry-type transformers, include internal inspection through access panels and doors.

      - Inspect bolted electrical connections for tightness.

      - Perform ground resistance test.

      - Perform insulation-resistance tests using a megohmmeter. Record results of primary and secondary winding-to-winding and winding-to-ground with test voltage.

        - For Windings’ Ratings from 0 to 600V: Use 1000V dc minimum test voltage; 500 megohms for dry-type and 100 megohms for liquid-filled transformers.

        - For Windings’ Ratings from 601 to 5000V: Use 2500V dc minimum test voltage; 5000 megohms for dry-type and 1000 megohms for liquid-filled transformers.

        - For Windings’ Ratings from 5000 to 35,000V: Use 5000V dc minimum test voltage; 25,000 megohms for dry-type and 5000 megohms for liquid-filled transformers.

    - Independent Testing Agency: Engage an independent electrical testing agency to test and certify medium-voltage transformer installations as specified in Section 26 08 00 - Acceptance Testing.

      - Electrical Contractor shall accompany the independent testing firm field service technician and assist as required during field tests.

    - Test Failures: Compare test results with specified performance or manufacturer’s data. Correct deficiencies identified by tests and retest. Verify that transformers meet specified requirements.

  - CLEANING

    - Upon completion of installation, inspect components. Remove paint splatters and other spots, dirt, and debris. Repair scratches and mars on finish to match original finish. Clean components internally using methods and materials recommended by manufacturer.

  - ADJUSTING

    - Adjust transformer taps to provide optimum voltage conditions at utilization equipment throughout normal operating cycle of facility. Record primary and secondary voltages and tap settings and submit with test results.

  - DEMONSTRATION AND TRAINING

Revise number of training hours to suit requirements. Delete non-applicable training items.

    - Training: Provide a factory-authorized service representative to demonstrate transformer operation and maintenance and provide training for Port maintenance personnel for one 8-hour work day at the job site location. Training shall include instructions on the following:

      - Safety precautions.

      - Features and construction of project transformers and accessories.

      - Routine inspection, test, and maintenance procedures.

      - Routine cleaning.

      - Features, operation, and maintenance of integral disconnect switches and protective devices.

      - Interpretation of readings of indicating and alarm devices.

      - Fuse selection.

      - Protective-relay setting considerations.

      - Features, operation, and maintenance of separable, insulated, connector system.

      - Tap-changing procedures.

    - Schedule training and provide notification to the Port at least 7 days in advance.

  - CERTIFICATE OF COMPLIANCE

    - A qualified factory-trained manufacturer’s representative shall certify in writing that equipment has been installed, adjusted and tested in accordance with manufacturer’s recommendations.

    - Installing Contractor shall provide three copies of certificates to the Port.

  - SUBMITTALS FOR CLOSEOUT

    - Final record drawings.

    - Operation and maintenance manuals.

    - Original certified test reports.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2, and revisions

01/29/2015 Revised Sole Source

02/15/2018 Revised requirement for differential relay protection.