READ THIS FIRST

The Engineer shall verify that the latest version of the Federal Aviation Administration Advisory Circular AC 150/5370-10, “Standards for Specifying Construction Of Airports” and that the latest version of the Federal Aviation Administration, Northwest Mountain Region Revision to AC 150/5370-10, “Standards for Specifying Construction Of Airports” are incorporated into this specification.

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Airport Underground Cable (FAA)” Work is shown in the Contract Documents.  Provide underground electrical and communications cable in duct and/or direct burial in trench, in accordance with the applicable provisions of FAA Item L-108, Underground Power Cable for Airports, attached hereto.

    - All or a portion of the work covered by this Section is to be conducted within the Air Operations Area (AOA) at Sea-Tac International Airport. Restrictions and conditions necessary to maintain airfield and aircraft safety as required by FAA regulations, and as required to maintain efficient airport operations, may impose limitations upon the Contractor’s methods and procedures. Section 01 35 13.13 - Operational Safety on Airports During Construction lists the applicable conditions, limitations and regulations.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

    - NFPA 70 – National Electrical Code.

    - NFPA 780 – Standard for the Installation of Lightning Protection Systems.

    - MIL-S-23586F – Performance Specification: Sealing Compound (with Accelerator), Silicone Rubber, Electrical.

    - ANSI/IEEE STD 81 – IEEE Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System.

  - SUBMITTALS

    - Submit materials data in accordance with Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product data for 5000 Volt cable.

      - Product data for connectors and splice material.

      - Cable test results.

- NOT USED

- NOT USED

- NOT USED

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

## Item L-108 Underground Power Cable for Airports

## DESCRIPTION

108-1.1	This item shall consist of furnishing and installing underground cable in accordance with these specifications at the locations shown in the plans. This item shall include the excavation and backfill of the trench and the installation of cable and counterpoise wire in trench, duct or conduit. It shall include splicing, cable marking and testing of the installation and all incidentals necessary to place the cable in operating condition as a completed unit to the satisfaction of the Engineer. This item shall not include the installation of the duct or conduit.

## EQUIPMENT AND MATERIALS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

108-2.1	GENERAL

A.	Airport lighting equipment and materials covered by Federal Aviation Administration (FAA) specifications shall have the prior approval of the FAA, and are listed in Advisory Circular (AC) 150/5345-1, Approved Airport Equipment.

B.	All other equipment and materials covered by other referenced specifications shall be subject to acceptance through manufacturer's certification of compliance with the applicable specification, when requested by the Engineer.

108-2.2	CABLE. Underground cable shall conform to the requirements of AC 150/5345-7, Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits. If telephone control cable is specified, copper shielded, polyethylene insulated and jacketed, No. 19 AWG telephone cable conforming to the United States Department of Agriculture, Rural Electrification Administration (REA) Bulletin 345-14, REA Specification for Fully Color-Coded, Polyethylene Insulated, Double Polyethylene-Jacketed Telephone Cables for Direct Burial, shall be used.

Where counterpoise conductors are to be installed and where soil conditions would adversely affect bare copper wire, thermoplastic wire conforming to Fed. Spec. J-C-30, Type TW, 600 volt, may be used.

Cable type, size, number of conductors, strand and service voltage shall be specified in the plans and/or proposal.

108-2.3	BARE COPPER WIRE (COUNTERPOISE). Bare copper wire for counter-poise installations shall be stranded wire conforming to ASTM Specifications B 3 and B 8.

108-2.4	CABLE CONNECTIONS. In-line connections of underground primary cables shall be of the type called for in the plans or in the proposal and shall be one of the types listed below. When the plans or the proposal permit a choice of connection, the Contractor shall indicate in the bid the type of connection he proposes to furnish.

- The Cast Splice: A cast splice, employing a plastic mold and using epoxy resin equal to that manufactured by Minnesota Mining and Manufacturing Company, “Scotchcast” Kit No. 82--A, or as manufactured by Hysol Corporation, “Hyseal Epoxy Splice” Kit No. E1135, Or Approved Equal for potting the splice is approved. This means of splicing is the only type approved for telephone control cable.

Competition waiver to be submitted to CPO for Joy Manufacturing Company to be the only approved product for the Port.

B.	The Vulcanized Splice: A vulcanized splice employing Joy Manufacturing Company’s Vulcanizing Kit No. X-1604-8, No Equal is approved for field vulcanized splices. The proper molds for various cable sizes shall be used.

C.	The Field-attached Plug-in Splice: Figure 3 of AC 150/5345-26, Specification for L-823 Plug and Receptacle, Cable Connectors, employing connector kits, is approved for field attachment to single conductor cable.

D.	The Factory-Molded Plug-in Splice: Specification for L-823 Connectors, Factory-Molded to Individual Conductors, are approved.

Competition waiver to be submitted to CPO for 3M Company to be the only approved product for the Port.

E.	The Taped Splice: Taped splices employing field-applied rubber, or synthetic rubber tape covered with plastic tape are approved. The rubber tape should meet the requirements of Mil. Spec. MIL-I-3825 and the plastic tape should comply with Mil. Spec. MIL-I-7798 or Fed. Spec. HH-I-595. In all the above cases, connections of cable conductors shall be made using crimp connectors utilizing a crimping tool designed. To make a complete crimp before the tool can be removed. No. 19 AWG telephone control wires may be connected by means of wrapped and soldered splice, 3M Company Moisture Proof UR Type Connector, No Equal, or by a method approved by the Engineer.

108-2.5	CONCRETE. Concrete for cable markers shall conform to Specification Item P-610, “Structural Portland Cement Concrete.”

## CONSTRUCTION METHODS

108-3.1	GENERAL. The Contractor shall install the specified cable at the approximate locations indicated in the airport lighting layout plans. The Engineer shall indicate specific locations.

Cable connections between lights will be permitted only at the light locations for connecting the underground cable to the primary leads of the individual insulating transformers. The Contractor shall be responsible for providing cable in continuous lengths for home runs or other long cable runs without connections, unless otherwise authorized in writing by the Engineer or shown in the plans.

108-3.2	INSTALLATION IN DUCT OR CONDUIT. This item includes the installation of the cable in duct or conduit as described below. The maximum number and voltage ratings of cables installed in each single duct or conduit, and the current-carrying capacity of each cable shall be in accordance with the latest National Electric Code, or the code of the local agency having jurisdiction.

The Contractor shall make no connections or joints of any kind in cables installed in conduits or ducts.

The duct or conduit shall be installed as a separate item in accordance with Item L-110, “Installation of Airport Underground Electrical Duct.” The Contractor shall make sure that the duct is open, continuous and clear of debris before installing cable. The cable shall be installed in a manner to prevent harmful stretching of the conductor, injury to the insulation, or damage to the outer protective covering. The ends of all cables shall be sealed with moisture-seal tape before pulling into the conduit and it shall be left sealed until connections are made. Where more than one cable is to be installed in a duct under the same contract, all cable shall be pulled in the duct at the same time. The pulling of a cable through ducts or conduits may be accomplished by hand winch or power winch with the use of cable grips or pulling eyes. Pulling tensions should be governed by recommended standard practices for straight pulls or bends. A lubricant recommended for the type of cable being installed shall be used where pulling lubricant is required. Duct or conduit markers temporarily removed for excavations shall be replaced as required.

108-3.3	TRENCHING. Where turf is well established and the sod can be removed, it shall be carefully stripped and properly stored. Trenches for cables may be excavated manually or with mechanical trenching equipment. Walls of trenches shall be essentially vertical so that a minimum of shoulder surface is disturbed. Road patrols or graders shall not be used to excavate the trench with their blades. The bottom surface of trenches shall be essentially smooth and free from coarse aggregate. Unless otherwise specified, cable trenches shall be excavated to a minimum depth of 30 inches (45 cm) below finished grade, except as follows:

A.	When off the airport or crossing under a roadway or driveway, the minimum depth shall be 24 inches (90 cm) unless otherwise specified.

B.	Minimum cable depth when crossing under a railroad track, shall be 42 inches (105 cm) unless otherwise specified.

The Contractor shall excavate all cable trenches to a width not less than 6 inches (150 mm). The trench shall be widened where more than two cables are to be installed parallel in the same trench. Unless otherwise specified in the plans, all cables in the same location and running in the same general direction shall be installed in the same trench.

When rock excavation is encountered, the rock shall be removed to a depth of at least 3 inches (75 mm) below the required cable depth and it shall be replaced with bedding material of earth or sand containing no mineral aggregate particles that would be retained on a 1/4 inch (6 mm) sieve. The Contractor shall ascertain the type of soil or rock to be excavated before bidding. All excavation shall be unclassified.

108-3.4	INSTALLATION IN TRENCHES. The Contractor shall not use a cable plow for installing the cable. Mechanical cable-laying equipment may be used in conjunction with a trenching machine if specified on project plans and specifications; and it should provide for physical inspection of cable prior to backfilling. Sharp bends or kinks in the cable shall not be permitted.

Cables shall be unreeled in place alongside or in the trench and shall be carefully placed along the bottom of the trench. The cable shall not be unreeled and pulled into the trench from one end.

Where two or more cables are laid parallel in the same trench, they shall be placed laterally a minimum distance of 3 inches (75 mm) apart, and the trench shall be widened sufficiently to accomplish this.

Cables crossing over each other shall have a minimum of 3 inch (75 mm) vertical displacement with the topmost cable depth at or below the minimum required depth below finished grade.

Not less than 1 foot (30 cm) of cable slack shall be left on each side of all connections, insulating transformers, light units and at all other points where cable is connected to field equipment. The slack cable shall be placed in the trench in a series of S-curves. Additional slack cable shall be left in runway light bases, handholes, manholes, etc., where it is required to bring the cable above ground level to make connections. The amount of slack cable shall be stipulated by the Engineer, or as shown in the plans and specifications.

108-3.5	BACKFILLING. After the cable has been installed, the trench shall be 3 inches (75 mm) deep, loose measurement and shall be either earth or sand containing no mineral aggregate particles that would be retained on a 1/4 inch (6 m) sieve. This layer shall not be compacted. The second layer shall be 5 inches (125 mm) deep, loose measurement, and shall contain no particles that would be retained on a 1 inch (25.0 mm) sieve. The remainder of the backfill shall be excavated or imported mineral and shall not contain stone or aggregate larger than 4 inches (100 mm) maximum diameter. The third and subsequent layers of the backfill shall not exceed 8 inches (200 mm) in maximum depth, loose measurement.

The second, and subsequent layers shall be thoroughly tamped and compacted to at least the density of the adjacent undisturbed soil, and to the satisfaction of the Engineer. If necessary to obtain the desired compaction, the backfill material shall be moistened or aerated as required.

Trenches shall not be excessively wet and shall not contain pools of water during backfilling operations. The trench shall be completely backfilled and tamped level with the adjacent surface, except that when sod is to be placed over the trench, the backfilling shall be stopped at a depth equal to the thickness of the sod to be used, with proper allowance for settlement. Any excess excavated material shall be removed and disposed of in accordance with instructions issued by the Engineer.

108-3.6	RESTORATION. Where sod has been removed, it shall be replaced as soon as possible after the backfilling is completed. All areas disturbed by the trenching, storing of dirt, cable laying, pad construction and other work shall be restored to its original condition. The restoration shall include any necessary topsoiling, fertilizing, liming, seeding, sodding, sprigging, or mulching. All such work shall be performed in accordance with the FAA standard turfing specifications. The Contractor shall be held responsible for maintaining all disturbed surfaces and replacements until final acceptance.

108-3.7	CABLE MARKERS. The location of runway light circuits shall be marked by a concrete slab marker, 2 feet (60 cm) square and 4 inches (100 mm) thick, extending approximately 1 inch (25 mm) above the surface. Each cable run from the line of runway lights to the equipment vault shall also be marked at approximately every 200 feet (60 m) along the cable run, with an additional marker at each change of direction of cable run. All other cable buried directly in the earth shall be marked in the same manner. The Contractor shall not install slab markers where cable lies in straight lines between obstruction light poles which are spaced 300 feet (90 m) apart, or less. Cable markers shall be installed immediately above the cable. The Contractor shall impress the word “cable” and directional arrows on each cable marking slab. The letters shall be approximately 4 inches (100 mm) high and 3 inches (75 mm) wide, with width of stroke 1/2 inch (12 mm) and 1/4 inch (6 mm) deep.

The location of each underground cable connection, except at lighting units or insulating transformers, shall be marked by a concrete marker slab placed above the connection. The Contractor shall impress the word “splice” on each slab. He also shall impress additional circuit identification symbols on each slab if so desired by the Engineer.

108-3.8	SPLICING. Connections of the type shown in the plans shall be made by experienced personnel regularly engaged in this type of work and shall be made as follows:

A.	Cast Splices: These shall be made by using crimp connectors for jointing conductors. Molds shall be assembled and the compound shall be mixed and poured in accordance with manufacturer's instructions and to the satisfaction of the Engineer.

B.	Vulcanized Splices: These shall be made by using crimp connectors for joining conductors. The splice shall be made, using compounds furnished by the manufacturer, in accordance with his/her instructions and to the satisfaction of the Engineer.

C.	Field-attached Plug-in Splices: These shall be assembled in accordance with manufacturer’s instructions. These splices shall be made by plugging directly into mating connectors. In all cases the joint where the connectors come together shall be wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches (37 mm) on each side of the joint.

D.	Factory-Molded Plug-in Splices: These shall be made by plugging directly into mating connectors. In all cases, the joint where the connectors come together shall be wrapped with at least one layer of rubber or synthetic rubber tape and one layer of plastic tape, one-half lapped, extending at least 1-1/2 inches (37 mm) on each side of the joint.

E.	Taped Splices: A taped splice shall be made in the following manner:

Bring the cables to their final position and cut so that the conductors will butt. Remove insulation and jacket allowing for bare conductor of proper length to fit compression sleeve connector with 1/4 inch (6 mm) of bare conductor on each side of the connector. Use a sharp knife to pencil insulation and jacket at approximately the same angle as a pencil point. Care must be taken to avoid nicking or injuring the conductor during removal of insulation or penciling. Do not use emery paper on splicing operation since it contains metallic particles. The copper conductors shall be thoroughly cleaned. Join the conductors by inserting them equidistant into the compression connection sleeve. Crimp conductors firmly in place with crimping tool that requires a complete crimp before tool can be removed. Test the crimped connection by pulling on the cable. Scrape the insulation to assure that the entire surface over which the tape will be applied (plus 3 inches (75 mm) on each end) is clean. After scraping wipe the entire area with a clean lint-free cloth. Do not use solvents.

Apply high-voltage rubber tape one-half lapped over bare conductor. This tape should be tensioned as recommended by the manufacturer. Voids in the connector area may be eliminated by highly elongating the tape stretching it just short of its breaking point. Throughout the rest of the splice less tension should be used. Always attempt to exactly half-lap to produce a uniform buildup. Continue buildup to 1-1/2 times cable diameter over the body of the splice with ends tapered a distance of approximately 1 inch (25 mm) over the original jacket. Cover rubber tape with two layers of vinyl pressure-sensitive tape one-half lapped. Do not use glyptol or lacquer over vinyl tape as they react as solvents to the tape. No further cable covering or splice boxes are required.

If shielded cable is to be spliced, prepare cable as for a regular taped splice, except that the neoprene jacket shall be removed a distance not less than 5 inches (125 mm) from the beginning of the penciled portion. Carefully unwrap the shielding tape from that portion where jacket has been removed and cut off so that it extends about 1 inch (25 mm) from end of the jacket. Proceed with the taped splice as described above and tape up to 1/4 inch (6 mm) from the shield on both ends. Build up rubber tape to a thickness equal to the insulation thickness or 5/16 inch (9 mm) over connector.

Competition waiver to be submitted to CPO for Scotch to be the only approved product for the Port.

Next wrap one-half lapped layer of semi-conducting tape (Scotch No. 13 Semi-Conducting Tape, No Equal) over splicing tape and 1/4 inch (6 mm) onto the shielding tape. Wrap a fine, flat shielding braid one-half lapped over the splice extending 1/2 inch (12 mm) onto the metallic shielding. Solder ends of braid to metallic shielding tape. A bonding wire, (Minimum No. 14 Stranded Copper) equal to the current carrying capacity of the metallic shield, should have the individual strands wrapped around the metallic shield at both ends of the splice. These strands should be tack soldered to the shield in several places. The cable sheath should be replaced by wrapping with two one-half lapped layers of vinyl tape extending 2 inches (50 mm) onto the cable jacket.

The above described splice is for a straight-through splice with continuity of shielding.

108-3.9	BARE COUNTERPOISE WIRE INSTALLATION AND GROUNDING FOR LIGHTNING PROTECTION. If shown in the plans or specified in job specifications, a stranded bare copper wire, No. 8 AWG minimum size, shall be installed for lightning protection of the underground cables. The bare counterpoise wire shall be installed in the same trench for the entire length of the insulated cables it is designed to protect and shall be placed at a distance of approximately 4 inches (100 mm) from the insulated cable. The counterpoise wire shall be securely attached to each light fixture base, or mounting stake. The counterpoise wire shall also be securely attached to copper or copper-clad ground rods installed not more than 1,000 feet (300 m) apart around the entire circuit. The ground rods shall be of the length and diameter specified in the plans, but in no case shall they be less than 8 feet (240 cm) long nor less than 5/8 inch (15 mm) in diameter.

The counterpoise system shall terminate at the transformer vault or at the power source. It shall be securely attached to the vault or equipment grounding system. The connections shall be made as shown in the project plans and specifications.

108-3.10	TESTING. The Contractor shall furnish all necessary equipment and appliances for testing the underground cable circuits after installation. The Contractor shall test and demonstrate to the satisfaction of the Engineer the following:

A.	That all lighting power and control circuits are continuous and free from short circuits.

B.	That all circuits are free from unspecified grounds.

C.	That the insulation resistance to ground of all non-grounded series circuits is not less than 50 megohms.

D.	That the insulation resistance to ground of all non-grounded conductors of multiple circuits is not less than 50 megohms.

E.	That all circuits are properly connected in accordance with applicable wiring diagrams.

F.	That all circuits are operable. Tests shall be conducted that include operating each control not less than 10 times and the continuous operation of each lighting and power circuit for not less than 1/2 hour.

## METHOD OF MEASUREMENT

108-4.1	Trenching shall be measured by the linear feet (meters) of trench, including the excavation, backfill and reconditioning, completed, measured as excavated and accepted as satisfactory.

When specified in the proposal, separate measurement shall be made for trenches of various specified widths.

108-4.2	Cable or counterpoise wire installed in shall be measured by the number of linear feet (meters) of cable or counterpoise wire installed in trenches, ready for operation and accepted as satisfactory. Separate measurement shall be made for each cable or counterpoise wire installed in trench.

108-4.3	Cable or counterpoise wire installed in duct or conduit shall be measured by the number of linear feet (meters) measured in place, completed, ready for operation and accepted as satisfactory.

Separate measurement shall be made for each cable or counterpoise wire installed in duct or conduit.

## BASIS OF PAYMENT

108-5.1	Payment will be made at the contract unit price for trenching cable and bare counterpoise wire installed in trench or duct in place by the Contractor and accepted by the Engineer. This price shall be full compensation for furnishing all materials and for all preparation and installation of these materials and for all labor, equipment, tools and incidentals necessary to complete this item.

A.	Payment will be made under:

1.	Item L-108-5.1 - Cable Trench--per linear foot

2.	Item L-108-5.2 - Underground Cable, installed in trench--per liner foot

3.	Item L-108-5.3 - Underground Cable, installed in duct or conduit--per linear foot

4.	Item L-108-5.4 - Bare Counterpoise Wire, installed in trench, including ground rods and ground connectors--per linear foot

5.

## MATERIAL REQUIREMENTS

- ASTM Specifications B 3 Soft or Annealed Copper Wire,

- ASTM Specifications B 8 Concentric-Lay-Stranded Cooper Conductor, Hard, Medium-Hard, or Soft,

- FAA,

- Federal Aviation Administration (FAA) specifications,

- FAA Item L-108, Underground Cable for Airports,

- Item L-110, “Installation of Airport Underground Electrical Duct,”

- Specification Item P-610, “Structural Portland Cement Concrete,”

- Advisory Circular (AC) 150/5345-1, Approved Airport Equipment,

- AC 150/5345-7 Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits,

- AC 150/5345-26 Specification for L-823 Plug and Receptacle Cable Connectors,

- AC 150/5345-26, Connectors, Factory-Molded to Individual Conductors,

- FAA standard turfing specifications,

- Fed. Spec. HH-I-595 Insulation Tape, Electrical, Pressure-Sensitive Adhesive, Plastic, for Low-Temperature Application,

- Fed.Spec.J-C-30 Cable and Wire, Electrical Power, Fixed Installation,

- Mil. Spec. MIL-I-3825, (rubber tape) Insulation Tape, Electrical, Self-Fusing, For Use in Electronics, Communications and Allied Equipment,

- Mil. Spec. MIL-I-7798, (plastic tape) Insulation Tape, Electrical, Pressure-Sensitive Adhesive, Plastic,

- National Electric Code, latest;

- United States Department of Agriculture, Rural Electrification Administration (REA) Bulletin 345-14, REA Specification for Fully Color-Coded, Polyethylene Insulated, Double Polyethylene-Jacketed Telephone Cables for Direct Burial,

End of Item