READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Low-Voltage Switchboards” Work is shown in the Contract Documents. This section includes service entrance and distribution switchboards rated 600V and less, 400 amp through 2000 amp, indoor, outdoor, circuit breaker and fused types.

    - DEFINITIONS

Retain abbreviations that remain after this section has been edited.

      - EMI: Electromagnetic interference.

      - GFCI: Ground-fault circuit interrupter.

      - RFI: Radio-frequency interference.

      - RMS: Root mean square.

      - SPDT: Single pole, double throw.

      - TVSS: Transient voltage surge suppressor.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - NEMA PB 2 (National Electrical Manufacturers Association) - Deadfront Distribution Switchboards,

    - NEMA 250 (National Electrical Manufacturers Association) - Enclosures for Electrical Equipment (1000 Volts Maximum),

    - NETA ATS (International Electrical Testing Association) - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems,

    - NFPA 70 (National Fire Protection Association) - National Electrical Code,

    - UL 891 (Underwriter's Laboratory) - Dead-Front Switchboards,

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: For each type of switchboard, overcurrent protective device, TVSS device, ground-fault protector, accessory, and component indicated. Include dimensions and manufacturers’ technical data on features, performance, electrical characteristics, ratings, and finishes.

      - Shop Drawings: For each switchboard and related equipment.

        - Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment. Show tabulations of installed devices, equipment features, and ratings. Include the following:

          - Enclosure types and details for types other than NEMA 250, Type 1.

          - Bus configuration, current, and voltage ratings.

          - Short-circuit current rating of switchboards and overcurrent protective devices.

Delete subparagraphs below if not required.

          - Descriptive documentation of optional barriers specified for electrical insulation and isolation.

          - Utility company’s metering provisions with indication of approval by utility company.

          - Mimic-bus diagram.

Delete subparagraph below if series rating of overcurrent protective devices is not used.

          - UL listing for series rating of installed devices.

          - Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

        - Wiring Diagrams: Diagram power, signal, and control wiring and differentiate between manufacturer-installed and field-installed wiring.

      - Manufacturer Seismic Qualification Certification: Submit certification that switchboards, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Section 26 05 48 - Seismic Controls for Electrical and Communication Work. Include the following:

        - Basis of Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

        - The term “withstand” means “the unit will remain in place without separation of internal and external parts during a seismic event and the unit will be fully operational after the event.”

      - Dimensioned Outline Drawings of Equipment Unit: Provide equipment weight, identify center of gravity and locate and describe mounting and anchorage provisions.

      - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Delete paragraph below if no mimic bus is specified.

      - Samples: Representative portion of mimic bus with specified finish, for color selection.

      - Field Test Reports: Submit written test reports and include the following:

        - Test procedures used.

        - Test results that comply with requirements.

        - Results of failed tests and corrective action taken to achieve test results that comply with requirements.

      - Manufacturer’s field service report.

Delete paragraph below if no mimic bus is specified.

      - Updated mimic-bus diagram reflecting field changes after final switchboard load connections have been made.

      - Maintenance Data: For switchboards and components to include in maintenance manuals specified in Division 1 General Requirements. In addition to requirements specified in Division 1 General Requirements , Section 01 78 23.13 - Operations and Maintenance Data include the following:

        - Routine maintenance requirements for switchboards and all installed components.

        - Manufacturer’s written instructions for testing and adjusting overcurrent protective devices.

        - Time-current curves, including selectable ranges for each type of overcurrent protective device.

  - QUALITY ASSURANCE

    - Listing and Labeling: Provide switchboards that are Listed and Labeled as defined in NFPA 70, Article 100 and marked for intended use for the location and environment in which they are installed.

    - Comply with NEMA 250, NEMA PB 2 and UL 891.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction. Particular attention is drawn to Article 384, “Switchboards and Panelboards”

Delete below if space is not a problem. Coordinate with Drawings.

    - Product Selection for Restricted Space: Drawings indicate maximum dimensions for switchboards, including clearances between switchboards, and adjacent surfaces and other items. Comply with indicated maximum dimensions.

    - Provide UL service entrance label for all equipment serving as service entrances.

  - DELIVERY, STORAGE, AND HANDLING

    - Deliver in sections of lengths that can be moved past obstructions in delivery path. Shipping splits shall not exceed 72-inches.

Delete one of first two paragraphs below or edit to suit Project.

    - Store indoors in clean dry space with uniform temperature to prevent condensation. Protect from exposure to dirt, fumes, water, corrosive substances, and physical damage.

    - If stored in areas subjected to weather, cover switchboards to provide protection from weather, dirt, dust, corrosive substances, and physical damage. Remove loose packing and flammable materials from inside switchboards; install electric heating (250W per section) to prevent condensation.

    - Handle switchboards according to NEMA PB 2.1.

  - PROJECT CONDITIONS

Modify paragraph below to describe specific requirements for moving switchboards into place. Where appropriate, indicate alterations to existing facilities that may be required to accommodate an indicated delivery path. Coordinate with Drawings.

    - Installation Pathway: Remove and replace access fencing, doors, lift-out panels, and structures to provide pathway for moving switchboards into place.

Delete paragraph and subparagraphs below if no existing utilities.

    - Existing Utilities: Do not interrupt utilities serving facilities occupied by the Port or others unless permitted under the following conditions and then only after arranging to provide temporary utility services according to requirements indicated:

      - Notify the Engineer not less than seven days in advance of proposed utility interruptions.

      - Do not proceed with utility interruptions without the Engineer’s written permission.

      - Coordinate with requirements specified in Section 01 50 00 - Temporary Facilities and Controls for temporary utilities

      - Field Measurements: Verify dimensions by field measurements.

Specify unusual environmental or service conditions here. Otherwise, indicate typical environmental conditions as follows: For switchboards installed outdoors, indicate minimum ambient temperature and expected humidity range.

    - Environmental Limitations: Rate equipment for continuous operation under the following, unless otherwise indicated:

      - Ambient Temperature: Not exceeding 104°F (40°C).

      - Altitude: Not exceeding 1000 feet.

      - [Insert unusual service conditions].

  - COORDINATION

Edit paragraph below to delete or add types of construction and encumbrances that affect switchboard installation.

    - Coordinate layout and installation of switchboards and components with other construction, including conduit, piping, equipment, and adjacent surfaces. Maintain required clearances for equipment access doors and panels, workspace clearances, and maintenance clearances for mechanical equipment.

    - Coordinate size and location of concrete bases. Refer to Section 03 30 00 - Cast-in-Place Concrete for concrete, reinforcement, and formwork requirements.

    - Provide dedicated electrical equipment space in accordance with NEC 110-26.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals. Coordinate with Section 26 28 13 - Fuses for quantities of spare fuses to be provided.

Fuses: [3] of each type and rating used. Include spares for the following:

Potential transformer fuses.

Control-power fuses.

Fuses and fusible devices for fused circuit breakers.

Fuses for fused switches.

Fuses for fused power-circuit devices.

Indicating Lights: [2] of each type installed.

Touchup Paint: [3] containers of paint matching enclosure finish, each one-half pint.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Cutler-Hammer; Division of Eaton.

      - General Electric (only if rated for 40ºC ambient operation).

      - Square D Co;

      - Or Approved Equal.

  - MANUFACTURED UNITS

Types described below include service and distribution switchboards most commonly applied. Select types required for Project from options in paragraphs and subparagraphs below. Coordinate with Drawings. If more than one type is required, identify by drawing identification number.

Coordinate type of switchboard with type of overcurrent protective devices and with switchboard arrangement and available space. Consult manufacturer to determine layout requirements.

    - Switchboards shall not require side or rear access unless engineering considerations dictate otherwise.

    - Front-Connected, Front-Accessible Switchboard: [Panel-mounted] [Fixed, individually mounted] main device, panel-mounted branches, and with sections rear aligned.

    - Front- and Side-Accessible Switchboard: Fixed, individually mounted main device, panel-mounted branches, and with sections rear aligned.

    - Front- and Rear-Accessible Switchboard: Front and rear aligned, with features as follows:

      - Main Devices: [Fixed, individually] [Drawout] [Panel] mounted.

Select mounting of branch devices from options in two subparagraphs below.

      - Branch Devices: Panel mounted through 800 amps.

      - Branch Devices: Fixed, individual compartments above 800 amps.

Coordinate paragraphs below with Drawings. Delete rating data if on Drawings.

Select one system voltage from paragraph below or insert appropriate system voltage.

    - Nominal System Voltage: [480Y/277 Volts, 3-phase, 4-wire.] [208 Y/120 Volts, 3-phase, 4-wire.]

    - Seismic Rating: Refer to Section 26 05 48 – Seismic Controls for Electrical and Communication Work.

    - Operating Temperature: The entire switchboard shall be designed for continuous operation at nameplate rated values in an ambient temperature of 40C.

      - Maximum bus temperature shall not exceed 65C rise over 40C ambient.

Select applicable bus rating from below or insert appropriate bus rating.

    - Main-Bus Continuous: [2000A] [1600A] [1200A] rating.

  - FABRICATION AND FEATURES

    - Enclosure: Steel: [NEMA 250, TYPE 1] [NEMA 250, Type 3R] [NEMA 250, Type 3R, with interior-lighted walk-in aisle].

    - Enclosure Finish for Outdoor Units: Factory-applied finish in manufacturer’s standard color, including undersurfaces treated with corrosion-resistant undercoating.

    - Enclosure Finish for Indoor Units: Factory-applied finish in manufacturer’s standard gray finish over a rust-inhibiting primer on treated metal surface.

Delete paragraph below if not required.

    - Barriers: Between adjacent switchboard sections.

Select one or both paragraphs below to specify optional features.

Add internal barriers and extra insulation to isolate energized components, such as buses and vertical sections, if required to protect against damage from arcing ground faults.

    - Insulation and isolation for main and vertical buses of feeder sections.

    - Insulation and isolation for main bus of main section and main and vertical buses of feeder sections.

Heaters and controls below usually specified for outdoor switchboards are sometimes specified for indoor units.

    - Space Heaters: Factory-installed electric space heaters of sufficient wattage in each vertical section to maintain enclosure temperature above expected dew point.

Select control and power source from options in subparagraphs below. Where overcurrent devices are mounted on both sides of a central walk-in corridor, more than one thermostat may be required.

      - Space-Heater Control: Thermostats to maintain temperature of each section above expected dew point.

      - Space-Heater Power Source: [Transformer, factory installed in switchboard] [120V external branch circuit].

    - Utility Metering Compartment: Fabricated compartment and section complying with utility company’s requirements. If separate vertical section is required for utility metering, match and align with basic switchboard.

    - Metering: Make provisions for remote monitoring and revenue metering of main and feeder breakers that are compatible with EATON PXM 2260 metering over airport-wide TCP/IP Ethernet backbone. All metering shall be revenue grade, .5% accuracy, in compliance with WAC and RCW requirements.

Pull sections in paragraph below are often required when incoming supply is beneath switchboard.

    - Bus Transition and Incoming Pull Sections: Matched and aligned with basic switchboard.

Delete one or both paragraphs below if no rear access or if standard bolted covers are adequate for rear and some front compartments.

    - Removable, Hinged Rear Doors and Compartment Covers: Secured by captive thumb screws, for access to rear interior of switchboard.

    - Hinged Front Panels: Allow access to circuit breaker, metering, accessory, and blank compartments.

    - Pullbox on Top of Switchboard: Include the following features:

      - Adequate ventilation to maintain temperature in pullbox within same limits as switchboard.

Delete subparagraph below if top-mounted, circuit-breaker removal mechanism is not used.

      - Set back from front to clear circuit breaker removal mechanism.

      - Removable covers shall form top, front, and sides. Top covers at rear shall be easily removable for drilling and cutting.

      - Bottom shall be insulating, fire-resistive material with separate holes for cable drops into switchboard.

      - Cable supports shall be arranged to facilitate cabling and adequate to support cables indicated, including those for future installation.

    - Buses and Connections: Three-phase, four-wire, unless otherwise indicated. Include the following features:

      - Phase- and Neutral-Bus Material: Hard-drawn copper of 98 percent conductivity with feeder circuit-breaker line connections.

Delete first subparagraph below if front-access sections are specified.

      - Load Terminals: Insulated, rigidly braced, silver-plated, copper runback bus extensions equipped with pressure connectors for outgoing circuit conductors. Provide load terminals for future circuit-breaker positions at full ampere rating of circuit-breaker position.

      - Ground Bus: 1/4-by-2-inch minimum size, drawn-temper copper of 98 percent conductivity, equipped with pressure connectors for feeder and branch-circuit ground conductors. For busway feeders, extend insulated equipment grounding cable to busway ground connection and support cable at intervals in vertical run.

      - Contact Surfaces of Buses: Silver plated. NO ALUMINUM BUS WILL BE ALLOWED.

      - Main Phase Buses, Neutral Buses, and Equipment Ground Buses: Uniform capacity for entire length of switchboard’s main and distribution sections. Provide for future extensions from both ends.

Delete subparagraph below if optional barriers are not specified.

      - Isolation Barrier Access Provisions: Permit checking of bus-bolt tightness.

      - Neutral Buses: 100 percent of the ampacity of the phase buses, unless otherwise indicated, equipped with pressure connectors for outgoing circuit neutral cables. Bus extensions for busway feeder neutral bus are braced.

Delete paragraph below if future provisions are not required.

    - Future Devices: Equip compartments with mounting brackets, supports, bus connections, and appurtenances at full rating of circuit-breaker compartment.

Insulation may not be required by authorities having jurisdiction. Delete below unless Project conditions require additional bus insulation. Uninsulated buses are standard.

    - Bus-Bar Insulation: Factory-applied, flame-retardant, 105°C minimum tape wrapping of individual bus bars or flame-retardant, spray-applied insulation of same temperature rating.

  - TVSS DEVICES

Delete this Article if not applicable.

    - IEEE C62.41, integrally mounted, plug-in style, solid-state, parallel-connected, sine-wave tracking suppression and filtering modules. UL 1449, second edition, short-circuit current rating matching or exceeding the switchboard short-circuit rating.

      - Fabrication using bolted compression lugs for internal wiring.

      - Arrangement with wire connections to phase buses, neutral bus, and ground bus.

      - LED indicator lights for power and protection status.

      - Form-C contacts rated at 5 A and 250-V ac, one normally open and one normally closed, for remote monitoring of system operation. Contacts shall reverse position on failure of any surge diversion module or on opening of any current-limiting device. Coordinate with building power monitoring and control system.

Edit and select ratings and protection modes in paragraphs and associated subparagraphs below to suit Project.

    - Peak Single-Impulse Surge Current Rating: 80 kA per mode/160 kA per phase.

    - Protection modes and UL 1449 SVR for grounded wye circuits with 480Y/277 OR 208Y/120 -V, three-phase, four-wire circuits shall be as follows:

      - Line to Neutral: 800 V for 480Y/277 OR 400 V for 208Y/120.

      - Line to Ground: 800 V for 480Y/277 OR 400 V for 208Y/120.

      - Neutral to Ground: 800 V for 480Y/277 OR 400 V for 208Y/120

    - Protection modes and UL 1449 SVR for 240/120-V, three-phase, four-wire circuits with high leg shall be as follows:

      - Line to Neutral: 400 V, 800 V from high leg.

      - Line to Ground: 400 V.

      - Neutral to Ground: 400 V.

    - Protection modes and UL 1449 SVR for 240-, 480-, or 600-V, three-phase, three-wire, delta circuits shall be as follows:

      - Line to Line: 2000 V for 480 V OR1000 V for 240 V.

      - Line to Ground: 1500 V for 480 V OR 800 V for 240 V.

    - Minimum single-impulse current rating shall be as follows:

      - Line to Neutral: 100,000 amps.

      - Line to Ground: 100,000 amps.

      - Neutral to Ground: 50,000 amps.

    - Protection modes shall be as follows:

      - Line to neutral.

      - Line to ground.

      - Neutral to ground.

Edit paragraph below to suit Project.

    - EMI/RFI Noise Attenuation Using 50-ohm Insertion Loss Test: 55 dB at 100 kHz.

Reference: IEEE C62.41

    - UL 1449 clamping levels shall not exceed [400V, line to neutral and line to ground on 208Y/120V systems] [800V, line to neutral and line to ground on 480Y/277V systems].

Select options below to suit Project.

    - Accessories shall include the following:

      - Form-C contacts, one normally open and one normally closed, for remote monitoring of system operation. Contacts to reverse position on failure of any surge diversion module.

      - Audible alarm activated on failure of any surge diversion module.

      - Six-digit transient-counter set to totalize transient surges that deviate from the sine-wave envelope by more than 125V.

  - OVERCURRENT PROTECTIVE DEVICES

    - Coordinate trip curves so that faults and shorts will clear at the nearest overcurrent device without tripping upstream devices.

Main circuit breakers are preferred over fused switches for switchboard mains through 1200A, and are to be individually mounted in compartments to isolate them from group mounted feeder breakers. This applies to both single main and multiple main (6 max) configurations.

    - Fused bolted pressure switches may be used for mains 1200A and above where required for interrupting capacity, current limiting, or coordination.

    - Feeder breakers rated 800A and less shall be group mounted.  Feeder breakers rated for greater than 800 amps shall be mounted in individual compartments.

    - Fused switches may be applied up to, but not including, 1200A rating where required for interrupting capacity and/or current limiting.

Coordinate this Article with schedules and Drawings.

    - Molded-Case Circuit Breaker: NEMA AB 1, with interrupting capacity to meet available fault currents.

      - Ampacity of Molded Case Circuit Breakers may be up to but not including 1200 amps. Comply with UL 489, with interrupting capacity to meet available fault currents.

      - Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

      - Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

      - Electronic Trip Unit Circuit Breakers: RMS sensing; field-replaceable rating plug; with the following field-adjustable settings:

        - Instantaneous trip.

        - Long- and short-time pickup levels.

        - Long- and short-time time adjustments.

        - Ground-fault pickup level, time delay, and I2t response.

      - Current-Limiting Circuit Breakers: Frame sizes 400A and larger; let-through ratings less than NEMA FU 1, RK-5.

      - Integrally Fused Circuit Breakers: Thermal-magnetic trip element with integral limiter-style fuse listed for use with circuit breaker; trip activation on fuse opening or on opening of fuse compartment door.

      - GFCI Circuit Breakers: Single- and two-pole configurations with Class A ground-fault protection [6] mA trip sensitivity.

      - Ground-Fault Equipment Protection (GFEP) Circuit Breakers, where required: Class B ground-fault protection (30-mA trip).

    - Molded-Case Circuit-Breaker Features and Accessories: Standard frame sizes, trip ratings, and number of poles.

      - Lugs: Mechanical style, suitable for number, size, trip ratings, and material of conductors.

      - Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

      - Ground-Fault Protection: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.  Settings shall be provided by Engineer of Record.

      - Communication Capability: [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system.

      - Shunt Trip: 120V trip coil energized from separate circuit, set to trip at [75] percent of rated voltage.

      - Undervoltage Trip: Set to operate at 35 to 75 percent of rated voltage [without intentional] [with field-adjustable 0.1- to 0.6-second] time delay.

      - Auxiliary Switch: [One SPDT switch] [Two SPDT switches] with “a” and “b” contacts; “a” contacts mimic circuit-breaker contacts, “b” contacts operate in reverse of circuit-breaker contacts.

      - Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

      - Zone-Selective Interlocking: Integral with electronic trip unit; for interlocking ground-fault protection function.

    - Enclosed, Insulated-Case Circuit Breaker: Fully rated, encased-power circuit breaker with interrupting capacity rating to meet available fault current.

      - Rating range, 1200 amp to 2000 amp.

      - [Fixed] circuit-breaker mounting.

      - Two-step, stored-energy closing.

      - Microprocessor-based trip units with interchangeable rating plug, LED trip indicators, and the following field-adjustable settings:

        - Instantaneous trip.

        - Long- and short-time pickup levels.

        - Long- and short-time time adjustments with I2t response.

        - Ground-fault pickup level, time delay, and I2t response.

      - Remote trip indication and control.

      - Communication Capability: Integral communication module with functions and features compatible with power monitoring and control system.

      - Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

      - Zone-Selective Interlocking: Integral with electronic trip unit; for interlocking ground-fault protection function.

Select voltage from subparagraphs below to match control-power supply (if applicable)

      - Control Voltage: [125V] [250V] dc.

Select subparagraph above for dc control voltage and subparagraph below for ac control voltage.

      - Control Voltage: [125V] [250V] ac.

    - Bolted-Pressure Contact Switch: For 1200A frame sizes and above. Operating mechanism uses rotary-mechanical-bolting action to produce and maintain high clamping pressure on the switch blade after it engages the stationary contacts.

      - Main-Contact Interrupting Capability: Minimum of 12 times the switch current rating.

      - Operating Mechanism: Manual handle operation to close switch; stores energy in mechanism for opening and closing.

        - Electrical Trip: Operation of lever or push-button trip switch, or trip signal from ground-fault relay or remote-control device, causes switch to open.

        - Mechanical Trip: Operation of mechanical lever, push button, or other device causes switch to open.

      - Auxiliary Switches: Factory installed, single pole, double throw, with leads connected to terminal block, and including one set more than quantity required for functional performance indicated.

      - Service-Rated Switches: Labeled for use as service equipment.

      - Ground-Fault Relay: Comply with UL 1053; self-powered type with mechanical ground-fault indicator, test function, tripping relay with internal memory, and three-phase current transformer/sensor.

        - Configuration: Integrally mounted relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

        - Internal Memory: Integrates the cumulative value of intermittent arcing ground-fault currents and uses the effect to initiate tripping.

        - No-Trip Relay Test: Permits ground-fault simulation test without tripping switch.

        - Test Control: Simulates ground fault to test relay and switch (or relay only if "no-trip" mode is selected).

      - Open-Fuse Trip Indicating Device: Arranged to trip switch open if a phase fuse opens, mounted on panel.

    - Fused Switch: NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle. Fused switches may be applied up to, but not including, 1200-Amp rating where required for interrupting capacity and/or current limiting Fused bolted pressure switches may be used for mains 1200 Amp and above where required for interrupting capacity current limiting or coordination.

      - Rating: 1200 amp to 2000 amp.

  - INSTRUMENTATION

Edit paragraphs below to coordinate with requirements of project.

    - Multifunction Digital-Metering Monitor: Microprocessor-based unit suitable for three- or four-wire systems and with the following features:

      - Switch-selectable digital display of the following values with maximum accuracy tolerances as indicated:

        - Phase Currents, Each Phase: Plus or minus 1 percent.

        - Phase-to-Phase Voltages, Three Phase: Plus or minus 1 percent.

        - Phase-to-Neutral Voltages, Three Phase: Plus or minus 1 percent.

        - Kilowatts: Plus or minus 2 percent.

        - Kilovars: Plus or minus 2 percent.

        - Power Factor: Plus or minus 2 percent.

        - Frequency: Plus or minus 0.5 percent.

        - Megawatt Demand: Plus or minus 2 percent; demand interval programmable from 5 to 60 minutes.

        - Accumulated Energy, Megawatt Hours: Plus or minus 2 percent. Accumulated values unaffected by power outages up to 72 hours.

      - Mounting: Display and control unit flush or semiflush mounted in instrument compartment door.

    - Potential Transformers: IEEE C57.13; 120 V, 60 Hz, [single] [tapped] [double] secondary; disconnecting type with integral fuse mountings. Burden and accuracy shall be consistent with connected metering and relay devices.

    - Current Transformers: IEEE C57.13; 5 A, 60 Hz, secondary; [wound] [bushing] [bar or window] type; [single] [double] secondary winding and secondary shorting device. Burden and accuracy shall be consistent with connected metering and relay devices. Compatible with EATON PXM 2000 series meters.

    - Control-Power Transformers: Dry type, mounted in separate compartments for units larger than 3 kVA.

    - Current Transformers for Neutral and Ground-Fault Current Sensing: Connect secondary wiring to ground overcurrent relays, via shorting terminals, to provide selective tripping of main and tie circuit breaker. Coordinate with feeder circuit-breaker, ground-fault protection.

  - CONTROL POWER

    - Control Circuits: 120V, supplied through secondary disconnecting devices from control-power transformer.

Delete paragraph below if not required.

    - Electrically Interlocked Main and Tie Circuit Breakers: Two control-power transformers in separate compartments, with interlocking relays, connected to the primary side of each control-power transformer at the line side of the associated main circuit breaker. 120V secondaries connected through automatic transfer relays to ensure a fail-safe automatic transfer scheme.

    - Control-Power Fuses: Primary and secondary fuses for current-limiting and overload protection of transformer and fuses for protection of control circuits.

    - Control Wiring: Factory installed, with bundling, lacing, and protection included. Provide flexible conductors for #8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

  - ACCESSORY COMPONENTS AND FEATURES

Delete paragraph below unless drawout circuit breakers are used.

    - Accessory Set: Tools and miscellaneous items required for overcurrent protective device test, inspection, maintenance, and operation.

Delete one or both apparatus paragraphs below. Retain only for installations with drawout circuit breakers.

    - Circuit-Breaker Removal Apparatus: Furnish one portable, floor-supported, roller-based, elevating carriage arranged for movement of circuit breakers in and out of compartments for present and future circuit breakers.

    - Circuit-Breaker Removal Apparatus: Overhead circuit-breaker lifting device, mounted at top front of switchboard, with hoist and lifting yokes matching each drawout circuit breaker.

    - Spare-Fuse Cabinet: Suitably identified, wall-mounted, lockable, compartmented steel box or cabinet. Arrange for wall mounting.

  - Provisions for Expansion:

    - Make provisions for adding future sections.

- EXECUTION

  - PROTECTION

    - Temporary Heating: Apply temporary heat to maintain temperature according to manufacturer’s written instructions.

  - EXAMINATION

    - Examine elements and surfaces to receive switchboards for compliance with installation tolerances and other conditions affecting performance.

      - Proceed with installation only after unsatisfactory conditions have been corrected.

  - INSTALLATION

    - Install switchboards and accessories according to NEMA PB 2.1.

    - Support switchboards on concrete bases, 3-1/2” nominal thickness. Comply with mounting and anchoring requirements specified in Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

      - Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch centers around the full perimeter of concrete base.

      - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

      - Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

      - Install anchor bolts to elevations required for proper attachment to switchboards.

    - Provide yellow striping in front of all switchboards outlining required code working space.

    - Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.

    - Operating Instructions: Frame and mount the printed basic operating instructions for switchboards, including control and key interlocking sequences and emergency procedures. Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic. Mount on front of switchboards.

  - CONNECTIONS

Coordinate paragraphs below with Drawings.

    - Install equipment grounding connections for switchboards with ground continuity to main electrical ground bus.

    - Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A and UL 486B.

      - Mark lugs after torquing with red paint such that paint will be visibly disturbed if lugs are disturbed.

  - PROTECTION

    - Temporary Heating: Apply temporary heat to maintain temperature according to manufacturer’s written instructions.

  - IDENTIFICATION

    - Identify field-installed conductors, interconnecting wiring, and components as specified in Section 26 05 53 - Electrical Identification.

    - Identify switchboard name, designation, power source, source location and voltage.

    - Label each switchboard fused switch or circuit breaker with engraved laminated-plastic nameplate indicating current rating, load served and load location.

    - Provide warning and caution signs where indicated or required by the Authority Having Jurisdiction.

    - Equipment used in emergency systems shall be labeled “Suitable for use on emergency systems” per NEC 700-3.

    - For fused switches, apply label inside door cover identifying NEMA fuse class and size of fuses installed. Arrange fuses so rating information is readable without removing fuse.

Delete below if series-rated system is not specified. Series-rated is only acceptable when engineering considerations dictate.

    - For series-rated equipment, provide label reading “Caution - Series Rated System” to comply with NEC 110-22 and WAC 296-46-110. List circuit-breaker types approved for the series rating.

Delete below if not required.

    - Mimic Bus: Continuously integrated mimic bus factory applied to front of switchboard. Arrange in single-line diagram format, using symbols and letter designations consistent with final mimic-bus diagram. Coordinate mimic-bus segments with devices in switchboard sections to which applied. Produce a concise visual presentation of principal switchboard components and connections.

Modify below to require other types of presentation media if factory-painted mimic bus is not desirable.

    - Presentation Media: Painted graphics in color contrasting with equipment factory-finished background to represent bus and components complete with lettered designations.

  - FIELD QUALITY CONTROL

    - Prepare for acceptance tests as follows:

      - Test insulation resistance for each switchboard bus, component, connecting supply, feeder, and control circuit.

      - Test continuity of each circuit.

    - Testing: After installing switchboards demonstrate product capability and compliance with requirements.

      - Inspect accessible components for cleanliness, mechanical and electrical integrity, and damage or deterioration. Verify that temporary shipping bracing has been removed. Verify that no tools or loose parts are left in the equipment

      - Inspect bolted electrical connections for completion and tightness.

      - Perform a ground resistance test

      - Check the operation at interlocks and switch mechanism.

      - Procedures: Perform each visual and mechanical inspection and electrical test indicated in NETA ATS, Sections 7.1, 7.5, 7.6, 7.9, 7.10, 7.11, and 7.14 as appropriate. Certify compliance with test parameters.

      - Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

      - Megger test switchboard and feeders with all breakers open before energizing. Use 1000V Megger for 480V equipment and 500V megger for 208V equipment.

      - Verify proper phase rotation

      - Ensure viability of bonding jumper when switchboards are used as service entrances.

      - Check load balance. If load unbalance exceeds 10% notify the Engineer for remedial action required.

      - Verify continuity of equipment grounds and bonding jumper.

Select from options below to suit types of switchboards specified.

    - Infrared Scanning: Perform an infrared scan of switchgear two weeks after Substantial Completion and before final acceptance. Make bus joints and connections accessible to a portable scanner and perform scanning during a period of normal working load as advised by Port.

      - Instrument: Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

      - Record of Infrared Scanning: Prepare a certified report that identifies switchboards checked and that describes scanning results. Include notation of deficiencies detected, remedial action taken and observations after remedial action.

  - ADJUSTING

Paragraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

    - Set field-adjustable switches and circuit-breaker trip ranges.

  - CLEANING

    - On completion of installation, inspect interior and exterior of switchboards. Remove paint splatters and other spots. Vacuum dirt and debris; do not use compressed air to assist in cleaning. Repair exposed surfaces to match original finish.

  - STARTUP SERVICES

    - Engage a factory-authorized service representative to perform startup service.

    - Verify that switchboard is installed and connected according to the Contract Documents.

Revise first paragraph below if point-to-point verification of all internal control wiring is not required.

    - Verify that electrical control wiring installation complies with manufacturer’s submittal by means of point-to-point continuity testing. Verify that wiring installation complies with requirements in Division 26 Electrical Sections.

    - Complete installation and startup checks according to manufacturer’s written instructions.

  - DEMONSTRATION AND TRAINING

    - Engage a factory-authorized service representative to train Port maintenance personnel to adjust, operate, and maintain switchboard.

      - Train Port maintenance personnel a minimum of four hours on procedures and schedules for energizing and de-energizing, troubleshooting, servicing, and maintaining equipment and schedules.

      - Review data in maintenance manuals. Refer to Section 01 78 23.13 - Operations and Maintenance Data.

      - Schedule training with the Port with at least seven days’ advance notice.

  - OPERATION AND MAINTENANCE MANUALS

    - Comply with Section 01 78 23.13 - Operations and Maintenance Data and Part 1 of this specification.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Revised Reference to Other Sections