READ THIS FIRST

The Engineer shall verify that the latest version of the Federal Aviation Administration Advisory Circular AC 150/5370-10, “Standards for Specifying Construction Of Airports” and that the latest version of the “Errata Sheet for Advisory Circular (AC) 150/5370-10H, Standard Specifications for Construction of Airports” are incorporated into this specification.

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Installation of Airport Lighting Systems (FAA)” Work is shown in the Contract Documents.  Airport Lighting systems, shall be provided in accordance with the applicable provisions of FAA Item L-125, Installation of Airport Lighting Systems, attached hereto.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

    - TBD

  - SUBMITTALS

    - Submit materials data in accordance with Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

- NOT USED

- NOT USED

- NOT USED

End of Section

Revision History:

03/15/2020 New section from FAA AC 150/5370-10H including errata through 11/12/2019

- Item L-125 Installation of Airport Lighting Systems

*************************************************************************************

Item L-125 should be used to indicate type of lights, signs, approach lights and other lighting equipment included in project.  The plans and specifications should include sufficient information for the Contractor to procure and install any specified equipment.

Additional equipment types may be added with coordination with the FAA. Delete non-applicable equipment types.

Include information in light and sign schedules in the plans.

*************************************************************************************

DESCRIPTION

125-1.1 This item shall consist of airport lighting systems furnished and installed in accordance with this specification, the referenced specifications, and the applicable advisory circulars (ACs). The systems shall be installed at the locations and in accordance with the dimensions, design, and details shown in the plans. This item shall include the furnishing of all equipment, materials, services, and incidentals necessary to place the systems in operation as completed units to the satisfaction of the RPR.

EQUIPMENT AND MATERIALS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

125-2.1 General.

- Airport lighting equipment and materials covered by Federal Aviation Administration (FAA) specifications shall be certified under the Airport Lighting Equipment Certification Program in accordance with AC 150/5345-53, current version.  FAA certified airfield lighting shall be compatible with each other to perform in compliance with FAA criteria and the intended operation.   If the Contractor provides equipment that does not performs as intended because of incompatibility with the system, the Contractor assumes all costs to correct the system for to operate properly.

- Manufacturer's certifications shall not relieve the Contractor of their responsibility to provide materials in accordance with these specifications and acceptable to the RPR. Materials supplied and/or installed that do not comply with these specifications shall be removed, when directed by the RPR and replaced with materials, which do comply with these specifications, at the sole cost of the Contractor.

- All materials and equipment used shall be submitted to the RPR for approval prior to ordering the equipment. Submittals consisting of marked catalog sheets or shop drawings shall be provided. Clearly mark each copy to identify pertinent products or models applicable to this project. Indicate all optional equipment and delete non-pertinent data. Submittals for components of electrical equipment and systems shall identify the equipment for which they apply on each submittal sheet. Markings shall be clearly made with arrows or circles (highlighting is not acceptable). The Contractor shall be responsible for delays in the project accruing directly or indirectly from late submissions or resubmissions of submittals.

d. The data submitted shall be sufficient, in the opinion of the RPR, to determine compliance with the plans and specifications. The Contractor's submittals shall be submitted in [   a neatly bound, properly sized 3-ring binder, tabbed by specification section.    ] [   electronic PDF format, tabbed by specification section.    ] The RPR reserves the right to reject any or all equipment, materials or procedures, which, in the RPR’s opinion, does not meet the system design and the standards and codes, specified herein.

*********************************************************************************

The Engineer will select the format required for submission of the data. The engineer should specify the form in which submittals are to be received and number of copies

*********************************************************************************

e. All equipment and materials furnished and installed under this section shall be guaranteed against defects in materials and workmanship for a period of at least [   twelve (12) months   ] from final acceptance by the Owner. The defective materials and/or equipment shall be repaired or replaced, at the Owner's discretion, with no additional cost to the Owner.

*************************************************************************************

All LED light fixtures, with the exception of obstruction lighting (AC 150/5345-43) must be warranted by the manufacturer for a minimum of 4 years after date of installation inclusive of all electronics.” Obstruction lighting warranty is set by the individual manufacturer.

*************************************************************************************

EQUIPMENT AND MATERIALS

125-2.2 Conduit/Duct. Conduit shall conform to Specification Item L-110 Airport Underground Electrical Duct Banks and Conduits.

125-2.3 Cable and Counterpoise. Cable and Counterpoise shall conform to Item L-108 Underground Power Cable for Airports.

Competition waiver to be submitted to CPO for 3M Company to be the only approved product for the Port.

125-2.4 Tape. Rubber and plastic electrical tapes shall be Scotch Electrical Tape Numbers 23 and 88 respectively, as manufactured by 3M Company or an approved equal.

125-2.5 Cable Connections. Cable Connections shall conform to Item L-108 Installation of Underground Cable for Airports.

125-2.6 Retroreflective Markers. [   Retroreflective markers shall be type L-853 and shall conform to the requirements of AC 150/5345-39.    ] [   Not required.    ]

125-2.7 Runway and Taxiway Lights.  Runway and taxiway lights shall conform to the requirements of AC 150/5345-46. Lamps shall be of size and type indicated, or as required by fixture manufacturer for each lighting fixture required under this contract. Filters shall be of colors conforming to the specification for the light concerned or to the standard referenced.

Lights

| Type | Class | Mode | Style | Option | Base | Filter | Transformer | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |

*******************************************************************************

Indicate type of light, base and transformer including class, mode, style and option as appropriate for project.  On elevated lights indicate height.  Add rows to table as necessary to indicate all light types required for project. In Notes column indicate bulb type if that is an option as well as fixture height for edge lights.

See AC 150/5340-30 for design and spacing requirements of light system.

See AC 150/5345-46 for specific characteristics of each fixture type.

Indicate fixture height of elevated fixtures.

All text enclosed in brackets requires editing by the engineer.

See engineering FAA Engineering Brief No. 67 “Light Sources other than Incandescent and Xenon for Airport Lighting and Obstruction Lighting Fixtures for additional information on LED fixtures.

Installation details should be shown on the plans with fixtures shown in section view. See AC 150/5340-30 for examples of installation details.

*************************************************************************************

125-2.8 Runway and Taxiway Signs. Runway and Taxiway Guidance Signs should conform to the requirements of AC 150/5345-44.

Signs

| Type | Size | Style | Class | Mode | Notes |
| --- | --- | --- | --- | --- | --- |
| [ ] | [ ] | [ ] | [ ] | [ ] | [ ] |

*************************************************************************************

Indicate type, size, style class and mode of signs for project, adding rows as necessary.

See AC 150/5340-18 for guidance on sign legends and locations.

See AC 150/5345-44 for information about sign sizes, styles, class, and mode.

*************************************************************************************

125-2.9 Runway End Identifier Light (REIL). [   The REIL fixtures shall meet the requirements of AC 150/5345-51, Type [   L-849V   ][   L-849I   ], Style [   A   ][   B   ][   C   ][   D   ][   E   ][   F   ].    ] [   Not required.    ]

125-2.10 Precision Approach Path Indicator (PAPI). [   The light units for the PAPI shall meet the requirements of AC 150/5345-28, Type [   L-880   ][   L-881   ], Style [   A   ][   B   ], Class [   I   ][   II   ].    ] [   Not required.    ]

*************************************************************************************

Plans should indicate details for location and installation of REILs and PAPIs.  See AC 150/5340-30 for requirements for locating and installing REIL and PAPI equipment.

*************************************************************************************

125-2.11 Circuit Selector Cabinet. The circuit selector cabinet shall meet the requirements of AC 150/5345-5, Type L-847, [   one   ][   two   ][   three   ][   four   ] circuit control [   as indicated   ], Class [   A, indoor   ][   B, outdoor   ], Rating [   1, for 6.6 amperes   ][   2, for 20 amperes   ].

125-2.12 Light Base and Transformer Housings. Light Base and Transformer Housings should conform to the requirements of AC 150/5345-42. Light bases shall be Type [   L-867   ] [   L-868   ], Class [   1A   ] [   1B   ] [   2A   ] [   2B   ], Size [   A   ] [   B   ] [   C   ] shall be provided as indicated or as required to accommodate the fixture or device installed thereon. Base plates, cover plates, and adapter plates shall be provided to accommodate various sizes of fixtures.

*************************************************************************************

Use Type L-867 bases for applications not subject to aircraft or heavy vehicle loading. Use Type L-868 for applications subjected to aircraft or vehicle loading.

*************************************************************************************

125-2.13 Isolation Transformers. Isolation Transformers shall be Type [   L-830   ] [   L-831   ], size as required for each installation. Transformer shall conform to AC 150/5345-47.

Installation

************************************************************************************

Include construction and/or installation details on the plans.  Include project installation requirement in the specifications from AC 150/5345-30.

************************************************************************************

125-3.1 Installation.  The Contractor shall furnish, install, connect and test all equipment, accessories, conduit, cables, wires, buses, grounds and support items necessary to ensure a complete and operable airport lighting system as specified here and shown in the plans.

The equipment installation and mounting shall comply with the requirements of the National Electrical Code and state and local code agencies having jurisdiction.

The Contractor shall install the specified equipment in accordance with the applicable advisory circulars and the details shown on the plans.

[   Insert project specific installation information from AC 150/5345-30 as required.    ]

125-3.2 Testing.  All lights shall be fully tested by continuous operation for not less than 24 hours as a completed system prior to acceptance. The test shall include operating the constant current regulator in each step not less than 10 times at the beginning and end of the 24-hour test. The fixtures shall illuminate properly during each portion of the test.

125-3.3 Shipping and Storage. Equipment shall be shipped in suitable packing material to prevent damage during shipping.  Store and maintain equipment and materials in areas protected from weather and physical damage. Any equipment and materials, in the opinion of the RPR, damaged during construction or storage shall be replaced by the Contractor at no additional cost to the owner. Painted or galvanized surfaces that are damaged shall be repaired in accordance with the manufacturer’s recommendations.

125-3.4 Elevated and In-pavement Lights. Water, debris, and other foreign substances shall be removed prior to installing fixture base and light.

A jig or holding device shall be used when installing each light fixture to ensure positioning to the proper elevation, alignment, level control, and azimuth control. Light fixtures shall be oriented with the light beams parallel to the runway or taxiway centerline and facing in the required direction. The outermost edge of fixture shall be level with the surrounding pavement. Surplus sealant or flexible embedding material shall be removed. The holding device shall remain in place until sealant has reached its initial set.

METHOD OF MEASUREMENT

125-4.1 Reflective markers will be measured by the number installed as completed units in place, ready for operation, and accepted by the RPR. Runway and taxiway lights will be measured by the number of each type installed as completed units in place, ready for operation, and accepted by the RPR. Guidance signs will be measured by the number of each type and size installed as completed units, in place, ready for operation, and accepted by the RPR. Runway End Identifier Lights shall be measured by each system installed as a completed unit in place, ready for operation, and accepted by the RPR.

Precision Approach Path Indicator shall be measured by each system installed as a completed unit, in place, ready for operation, and accepted by the RPR. Abbreviated Precision Approach Path Indicator shall be measured by each system installed as a completed unit, in place, ready for operation, and accepted by the RPR.

*************************************************************************************

Delete non-applicable equipment types.  Additional equipment types may be added with coordination with the FAA.

*************************************************************************************

BASIS OF PAYMENT

125-5.1 Payment will be made at the Contract unit price for each complete runway or taxiway light, guidance sign, reflective marker, runway end identification light, precision approach path indicator, or abbreviated precision approach path indicator installed by the Contractor and accepted by the RPR. This payment will be full compensation for furnishing all materials and for all preparation, assembly, and installation of these materials, and for all labor, equipment, tools and incidentals necessary to complete this item.

Payment will be made under:

[   Item   ]                            [   Description   ] – [   each   ]

************************************************************************************

Add in item, description and measurement for all lights, signs included in project.

************************************************************************************

References

The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

Advisory Circulars (AC)

AC 150/5340-18	Standards for Airport Sign Systems

AC 150/5340-26	Maintenance of Airport Visual Aid Facilities

AC 150/5340-30	Design and Installation Details for Airport Visual Aids

AC 150/5345-5	Circuit Selector Switch

AC 150/5345-7	Specification for L-824 Underground Electrical Cable for Airport Lighting Circuits

AC 150/5345-26	Specification for L-823 Plug and Receptacle, Cable Connectors

AC 150/5345-28	Precision Approach Path Indicator (PAPI) Systems

AC 150/5345-39	Specification for L-853, Runway and Taxiway Retroreflective Markers

AC 150/5345-42	Specification for Airport Light Bases, Transformer Housings, Junction Boxes, and Accessories

AC 150/5345-44	Specification for Runway and Taxiway Signs

AC 150/5345-46	Specification for Runway and Taxiway Light Fixtures

AC 150/5345-47	Specification for Series to Series Isolation Transformers for Airport Lighting Systems

AC 150/5345-51	Specification for Discharge-Type Flashing Light Equipment

AC 150/5345-53	Airport Lighting Equipment Certification Program

Engineering Brief (EB)

EB No. 67	Light Sources Other than Incandescent and Xenon for Airport and Obstruction Lighting Fixtures

END OF ITEM L-125