READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Lighting Controls” Work is shown in the Contract Documents. This section includes the following:

      - Lighting Control Contactors.

      - Photoelectric Cells and Time Clocks.

      - Programmable lighting control systems, and relay panels.

      - Illumination level and motion sensors.

      - Emergency shunt relays.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - NFPA 70 (National Fire Protection Association) - National Electrical Code,

    - NFPA 101 (National Fire Protection Association) - Life Safety Code,

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: Include dimensions and data on features, components, and ratings for dimming controls. Include elevation views of front panels of control and indicating devices and control stations. Also include the following:

        - List of ballasts and lamp combinations compatible with dimmer controls, by manufacturer and catalog number.

        - Sound data, including results of operational tests of dimming controls.

        - Operational documentation for software and firmware.

      - Shop Drawings: Detail assemblies of standard components, custom assembled for specific application on Project. Indicate dimensions, weights, arrangement of components, and clearance and access requirements.

        - Wiring Diagrams: Detail specific systems tailored to this Project and differentiate between manufacturer-installed and field-installed wiring.

      - Manufacturer Certificates: Signed by manufacturers certifying that they comply with requirements.

      - Field Test Reports: Indicate and interpret test results for compliance with performance requirements.

      - Maintenance Data: For controls to include in maintenance manuals specified in Division 1 General Requirements. Include operation and maintenance manuals.

      - Warranties: Special warranties specified in this section.

  - QUALITY ASSURANCE

    - Listing and Labeling: Provide electrical components, devices, and accessories that are Listed and Labeled as defined in NFPA 70, Article 100 and marked for intended use for the location and environment in which they are installed.

    - Comply with 47 CFR 15, Subparts A and B, for Class A digital devices.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

  - SPECIAL WARRANTY

    - General Warranty: Special warranty specified in this Article shall not deprive Owner of other rights Owner may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

    - Special Warranty: Written warranty, executed by manufacturer agreeing to repair or replace components of dimming controls that fail in materials or workmanship within specified warranty period.

Below is an example only. Verify available warranties and length of warranty period with manufacturers selected.

    - Warranty Period: Two years from date of Substantial Completion.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Products: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

      - Contactors

        - Square D.; Division of Schneider Electric.

        - General Electric.

        - Cutler-Hammer; Division of Eaton.

        - Allen Bradley.

        - Or Approved Equal.

      - Time Clocks.

        - Tork

        - Intermatic.

        - Or Approved Equal.

      - Programmable Lighting Control Systems

The existing programmable lighting control system at the Airport is Microlite.

        - Microlite.

        - Square D.; Division of Schneider Electric.

        - Cutler-Hammer; Division of Eaton.

        - Or Approved Equal.

      - Illumination Level and Motion Sensors

        - Watt-Stopper; Division of Legrand.

        - SensorSwitch.

        - Mytech.

        - Or Approved Equal.

      - Dimmer Switches

        - Lutron.

        - Leviton.

        - Lightolier; Division of Philips.

        - Or Approved Equal.

  - CONTACTORS

    - Configuration: Electrically held with 20 Amp tungsten halogen rating, and 30 Amp ballast rating. Match branch circuit overcurrent protection considering derating for continuous loads.

    - Description: Electrically operated and mechanically held combination-type lighting contactors with nonfused disconnect, complying with NEMA ICS 2 and UL 508.

      - Current Rating for Switching: Listing or rating consistent with type of load served, including tungsten filament, inductive, and high-inrush ballast (ballast with 15 percent or less total harmonic distortion of normal load current).

      - Fault Current Withstand Rating: Equal to or exceeding the available fault current at the point of installation.

Specify coil operating voltage below.

    - Coil operating voltage: [120] [277] 60Htz.

    - Auxiliary Contacts: Field convertible contacts with normally open contacts and normally closed indicators.

    - Poles: As required to match circuit configuration. 12-pole maximum.

    - Provide field convertible contacts with N.O. and N.C. indicators.

    - Provide contactors with mounting brackets.

    - Enclosure: NEMA ICS 6 and NEMA 250, as required to match conditions. Fabricate enclosure from steel finished with gray. Interior NEMA Type 1, Exterior NEMA Type 3R.

  - PHOTOELECTRIC CELLS

    - Description: Solid state, with dry contacts rated for 1800-VA tungsten or 1000-VA inductive , to operate connected relay, contactor coils, or microprocessor input; complying with UL 773A.

    - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

    - Level Monitoring Range:  1-5 fc on, 3-15 fc off, with an adjustment for turn-on and turn-off levels within that range.

    - Photoelectric cells shall typically be conduit mounted.

    - Delay up to two minutes to prevent false switching.

    - Provide on/off adjustment by light level sensor.

    - Enclosure:  Heavy-duty die cast zinc, gasketed for maximum weather protection.

    - Cell:  Cadmium sulphide, epoxy coated.

    - Contacts:  Closed between dusk and dawn.

    - Temperature range:  -40°F to 140°F.

    - Manual bypass switch shall be installed in parallel to the photocell (keyed if accessible to general public).

    - For outdoor lighting, provide 60-minute timed on override in accessible location unless fog detection or time clock is included in photoelectric controller.

  - TIME CLOCKS

    - Multi-purpose, microprocessor based digital controller.

    - Eight channel with remote timed override, 365-day advance single and block holiday scheduling.

    - Astronomic dials with automatic day-light saving.

    - Program entities shall be made by mechanical pushbutton and acknowledgement of each entry into the unit.

    - Each channel shall have remote timed override.

  - PROGRAMMABLE LIGHTING CONTROL SYSTEMS

    - Low-voltage switching system consisting of switchable breakers and intelligent switches connected together by a dataline.

    - Microprocessor based digital controller.

    - Control devices shall consist of photosensor control modules and/or other low-voltage control devices.

    - All components and assemblies shall be factory pre-tested prior to installation.

    - Remote panels are to be UL listed under UL 916 energy management equipment.

    - All assemblies are to be in compliance with FCC emissions standards specified in Part 15, Subpart J, for Class A application.

  - DAYLIGHT-HARVESTING SWITCHING CONTROLS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Hubbell Building Automation, Inc.

      - Leviton Manufacturing Co., Inc.

      - Sensor Switch, Inc.

      - Watt Stopper.

      - Or Approved Equal.

    - Ceiling-Mounted Switching Controls: Solid-state, light-level sensor unit, with separate power pack, to detect changes in indoor lighting levels that are perceived by the eye.

    - Electrical Components, Devices, and Accessories:

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Operating Ambient Conditions: Dry interior conditions, 32 to 120 deg F.

      - Sensor Output: Contacts rated to operate the associated power pack, complying with UL 773A. Sensor is powered by the power pack.

      - Power Pack: Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13A tungsten at 120-V ac. Power pack shall be capable of multi-level switching of up to three zones based on light level inputs from single photocell.

      - Closed Loop Sensor Light-Level Monitoring Range: 1 to 1400 fc, with an adjustment for turn-on and turn-off levels within that range.

      - Open Loop Sensor Light Level Monitoring Range: 10-6000 fc, with an adjustment for turn-on and turn-off levels within that range.

      - Set-Point Adjustment: Equip with deadband adjustment of 25, 50, and 75 percent above the "on" set point, or provide with separate adjustable "on" and "off" set points.

      - Test Mode: User selectable, overriding programmed time delay to allow settings check.

      - Control Load Status: User selectable to confirm that load wiring is correct.

      - Indicator: Digital display to indicate footcandle level and LED status light.

  - DAYLIGHT-HARVESTING DIMMING CONTROLS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Sensor Switch

      - Hubbell Building Automation, Inc.

      - Leviton Mfg. Company Inc.

      - Watt Stopper.

      - Or Approved Equal.

    - System Description: Sensing daylight and electrical lighting levels, the system adjusts the indoor electrical lighting levels. As daylight increases, the lights are dimmed.

      - Lighting control set point is based on two lighting conditions:

        - When no daylight is present (target level).

        - When significant daylight is present.

      - System programming is done with two hand-held, remote-control tools.

        - Initial setup tool.

      - Tool for occupants to adjust the target levels by increasing the set point up to 25 percent, or by minimizing the electric lighting level.

    - Ceiling-Mounted Dimming Controls: Solid-state, light-level sensor unit, with separate controller unit, to detect changes in lighting levels that are perceived by the eye.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Sensor Output: 0- to 10-V dc to operate electronic dimming ballasts. Sensor is powered by controller unit.

      - Power Pack: Sensor has 24-V dc, Class 2 power source, as defined by NFPA 70. Capable of controlling two separate zones of lighting based on input from single photosensor.

      - Light-Level Sensor Set-Point Adjustment Range: 3-6000 fc.

  - ILLUMINATION LEVEL AND MOTION SENSORS

    - General Requirements for Sensors: Automatic-wall-switch occupancy sensor, suitable for mounting in a single gang switchbox.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Operating Ambient Conditions: Dry interior conditions, 32 to 120 deg F. Switch Rating: Not less than 800-VA fluorescent at 120 V, 1200-VA fluorescent at 277 V, and 800-W incandescent.

    - Wall-Switch Sensor:

      - Range: 180-degree field of view, coverage shall be adequate for application.

      - Sensing Technology: Dual technology.

      - Switch Type: Field selectable for automatic on or manual on, with automatic off.

      - Voltage: Match the circuit voltage.

      - Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

    - Illumination Level Sensors

      - Natural light level sensor fully integrated lighting control system.

      - User adjustable light level settings ranging from 10 - 1000 footcandles.

      - Adjustable dead-band settings.

      - LED display.

      - Control any lamping source.

      - Adjustable time delay, 0 to 2 hours.

There are several types of motion sensors. Ceiling mounted with full 360 degree coverage pattern, ceiling mounted for hallways and corridors, and switchbox occupancy sensors. All of these should be included in this specification. Power packs should also be included.

    - Motion Sensors

      - Passive Infra-red/Ultrasonic combined technology.

      - Choice of auto-on or manual-on operation.

      - Adjustable sensitivity and time delay settings.

      - Building management control system compatible.

      - Adjustable time delay, 0 to 2 hours.

  - INDOOR OCCUPANCY SENSORS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Leviton Manufacturing Co., Inc.

      - Lutron Electronics Co., Inc.

      - Sensor Switch, Inc.

      - Watt Stopper.

      - Or Approved Equal.

    - General Requirements for Sensors: Wall- or ceiling-mounted, solid-state indoor occupancy sensors with a separate power pack.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Operation: Unless otherwise indicated, turn lights on when coverage area is occupied, and turn them off when unoccupied; with a time delay for turning lights off, adjustable over a minimum range of 1 to 30 minutes.

      - Sensor Output: Contacts rated to operate the connected relay, complying with UL 773A. Sensor is powered from the power pack.

      - Power Pack: Dry contacts rated for 20-A ballast load at 120- and 277-V ac, for 13-A tungsten at 120-V ac, and for 1 hp at 120-V ac. Sensor has 24-V dc, 150-mA, and Class 2 power source, as defined by NFPA 70.

      - Mounting:

        - Sensor: Suitable for mounting in any position on a standard outlet box.

        - Relay: Externally mounted in a standard electrical enclosure.

        - Time-Delay and Sensitivity Adjustments: Recessed and concealed behind hinged door.

      - Indicator: LED status lights to show when motion is detected during testing and normal operation of sensor.

      - Bypass Switch: Override the "on" function in case of sensor failure.

    - Dual-Technology Type: Ceiling mounted; detect occupants in coverage area using PIR and ultrasonic detection methods. Trigger of either technology, turns lights on. Both technologies must detect vacancy in order for lights to turn off.

      - Sensitivity Adjustment: Separate for each sensing technology.

      - Detector Sensitivity: Detect occurrences walking motion and desktop motion.

      - Detection Coverage: Provide sensor layout to ensure complete room coverage. Ceiling mounted sensors shall have 360° of coverage.

      - Ceiling sensor shall be used in conjunction with manual wall switch. Verify compatibility of sensor and wall switch.

      - Sensor shall be capable of manual on/auto off function.

  - SWITCHBOX-MOUNTED OCCUPANCY SENSORS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Leviton Manufacturing Co., Inc.

      - Lutron Electronics Co., Inc.

      - NSi Industries LLC; TORK Products.

      - Sensor Switch, Inc.

      - Watt Stopper.

      - Or Approved Equal.

    - General Requirements for Sensors: Automatic-wall-switch occupancy sensor, suitable for mounting in a single gang switchbox.

    - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

    - Operating Ambient Conditions: Dry interior conditions, 32 to 120 deg F. Switch Rating: Not less than 800-VA fluorescent at 120 V, 1200-VA fluorescent at 277 V, and 800-W incandescent.

    - Wall-Switch Sensor:

      - Range: 180-degree field of view, coverage shall be adequate for application.

      - Sensing Technology: Dual technology.

      - Switch Type: Field selectable for automatic on or manual on, with automatic off.

      - Voltage: Match the circuit voltage.

      - Concealed, field-adjustable, "off" time-delay selector at up to 30 minutes.

  - MANUAL, MODULAR DIMMING CONTROLS

    - Description: Factory-fabricated equipment providing one to four channels of manual dimming control. Integrate controls and dimmers for mounting in a two- or three-gang wall box under a single wall plate.

    - Module Dimming Capability: Listed for control of type of lighting unit used.

      - Fluorescent Dimmers, 277V Circuits: Control lights smoothly over a minimum range of 100 to 5 percent of full brightness.

Subparagraph below is an example of typical ratings for manual, modular systems.

      - Unit Rating: 1900W, minimum; with each dimming channel rated 600W, minimum.

      - Wall-Plate Style and Finish: Coordinated with lighting controls specified in Division 26 Electrical Sections.

  - DAYLIGHT-HARVESTING DIMMING CONTROLS

    - System Description: Sensing daylight and electrical lighting levels, the system adjusts the indoor electrical lighting levels. As daylight increases, the lights are dimmed.

      - Lighting control set point is based on two lighting conditions:

        - When no daylight is present (target level).

        - When significant daylight is present.

      - System programming is done with two hand-held, remote-control tools.

        - Initial setup tool.

        - Tool for occupants to adjust the target levels by increasing the set point up to 25 percent, or by minimizing the electric lighting level.

    - Ceiling-Mounted Dimming Controls: Solid-state, light-level sensor unit, with separate controller unit, to detect changes in lighting levels that are perceived by the eye.

      - Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - Sensor Output: 0- to 10-V dc to operate electronic dimming ballasts. Sensor is powered by controller unit.

      - Power Pack: Sensor has 24-V dc, Class 2 power source, as defined by NFPA 70. Capable of controlling two separate zones of lighting based on input from single photosensor.

      - Light-Level Sensor Set-Point Adjustment Range: 3-6000 fc.

  - EMERGENCY SHUNT RELAY

    - Description: Normally closed, electrically held relay, arranged for wiring in parallel with manual or automatic switching contacts; complying with UL 924.

      - Coil Rating: Voltage to match lighting circuit.

  - LOW-VOLTAGE WIRING

    - Digital and Multiplexed Signal Wire: Shielded, twisted-pair cable as specified in Section 26 05 23 - Control/Signal Transmission Media.

    - Low-Voltage Control Cable: Multiple conductor, color-coded, #20 AWG copper, minimum.

      - Sheath: PVC, except in plenum-type spaces use sheath listed for plenums.

      - Ordinary Switch Circuits: Three conductors, unless otherwise indicated.

      - Switch Circuits with Pilot Lights or Locator Feature: Five conductors, unless otherwise indicated.

- EXECUTION

  - SENSOR INSTALLATION

    - Coordinate layout and installation of ceiling-mounted devices with other construction that penetrates ceilings or is supported by them, including light fixtures, HVAC equipment, smoke detectors, fire-suppression systems, and partition assemblies. Comply with device manufacturer’s recommendations for distance from HVAC equipment.

    - Install and aim sensors in locations to achieve not less than 90 percent coverage of areas indicated. Do not exceed coverage limits specified in manufacturer's written instructions.

    - Photoelectric Cells shall be oriented north, and shall be directed to avoid detection of artificial light source.

    - Install lighting contactors in NEMA enclosure appropriate for location. Provide disconnecting means and overcurrent protection at contactor enclosures.

    - Installation shall comply with sensor manufacturer’s recommendations.

  - CONTACTOR INSTALLATION

Coordinate this Article with Drawings.

    - Mount electrically held lighting contactors with elastomeric isolator pads to eliminate structure-borne vibration, unless contactors are installed in an enclosure with factory-installed vibration isolators.

    - Mount Contactors in NEMA enclosure rated for location.

    - Mount control equipment according to manufacturer’s written instructions and requirements in Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

  - CONTROL WIRING INSTALLATION

    - Install wiring as specified in Section 26 05 19 - 600 Volt or Less Wire and Cable for low-voltage connections and Section 26 05 23 - Control/Signal Transmission Media for digital circuits.

    - Wiring Method: Install all wiring in raceway as specified in Section 26 05 33 - Raceway and Boxes.

    - Bundle, train, and support wiring in enclosures.

    - Ground equipment.

    - Splices, Taps, and Terminations: Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

    - Connections: Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A.

  - IDENTIFICATION

    - Identify components and power and control wiring according to Section 26 05 53 - Electrical Identification.

    - Label lighting control panels with equipment designation, power source and circuit numbers, and power source location.

    - Label all relays and control devices.

  - FIELD QUALITY CONTROL

    - Manufacturer’s Field Services: Engage a factory-authorized service representative to test, adjust, and program programmable lighting control systems.

    - Schedule visual and mechanical inspections and electrical tests with at least seven days’ advance notice.

Delete non-applicable items below.

    - Inspect control components for defects and physical damage, testing laboratory labeling, and nameplate compliance with the Contract Documents.

    - Check tightness of electrical connections with torque wrench calibrated within previous six months. Use manufacturer’s recommended torque values.

    - Verify settings of photoelectric devices with photometer calibrated within previous six months.

    - Electrical Tests: Use particular caution when testing devices containing solid-state components. Perform the following according to manufacturer’s written instructions:

      - Continuity tests of circuits.

      - Operational Tests: Set and operate controls to demonstrate their functions and capabilities in a methodical sequence that cues and reproduces actual operating functions.

        - Include testing of dimming control equipment under conditions that simulate actual operational conditions. Record control settings, operations, cues, and functional observations.

    - Perform the following calibration, tests and inspections:

    - Occupancy Sensors: Automatic-wall-switch occupancy sensor, suitable for mounting in a single gang switchbox.

      - Visually check placement and aiming of sensors and LED activity.

      - Verify that wiring type, technique, connections, and polarity are correct.

      - Test sensor function:

        - Motion

          - Set sensitivity to Minimum. Set time delay to Minimum. Verify OFF.

          - Adjust sensitivity to desired setting. Verify ON with motion.

          - Adjust time delay to desired setting. Walk-test room for sensitivity.

        - Daylight Sensors

          - Visually check placement and aiming of sensors and LED display.

          - Verify that wiring type, technique, connections and polarity are correct.

          - All room finishes and furniture must be installed prior to start-up, calibration and testing. If a desk or table is within the area viewed by the photocell, then the desk should be unpacked and the surface cleaned prior to final calibration.

          - Any window treatment must be installed and operable prior to start-up. Blinds must be positioned as they would be under normal conditions.

          - Do no calibrate dimming controls under overcast skies. Controls adjusted under these conditions are likely to over-dim the lights under sunny conditions.

          - Calibrate and test sensor function:

            - Adjust deadband and cutoff levels based on project requirements.

            - Set light level to Minimum. Set sensitivity level to Minimum. Set time delay to Minimum. Verify OFF.

            - Adjust sensitivity to desired setting. Cover sensor lens. Verify ON.

            - Adjust Light Level to desired setting.

            - Adjust time delay to desired setting.

    - Correct deficiencies, make necessary adjustments, and retest. Verify that specified requirements are met.

    - Test Labeling: After satisfactory completion of tests and inspections, apply a label to tested components indicating test results, date, and responsible agency and representative.

    - Reports: Written reports of tests and observations. Record defective materials and workmanship and unsatisfactory test results. Record repairs and adjustments.

  - ADJUSTING

    - Occupancy Adjustments: When requested within 12 months from date of Substantial Completion, provide on-site assistance in adjusting sensors to suit actual occupied conditions. Provide up to two visits to Project during other-than-normal occupancy hours for this purpose.

    - For occupancy and motion sensors, verify operation at outer limits of detector range. Set time delay to suit Owner's operations.

    - For daylighting controls, adjust set points and deadband controls to suit Owner's operations.

  - CLEANING

    - Cleaning: Clean equipment and devices internally and externally using methods and materials recommended by manufacturers, and repair damaged finishes.

  - DEMONSTRATION

    - Engage a factory-authorized service representative to train Port maintenance personnel as specified below:

      - Train Port maintenance personnel on troubleshooting, servicing, adjusting, and maintaining equipment and schedules. Provide a minimum of two four-hour sessions on separate days for training. Use both classroom training and hands-on exercises.

      - Review data in maintenance manuals. Refer to Section 01 78 23.13 - Operations and Maintenance Data.

      - Schedule training with the Port with at least seven days’ advance notice.

  - ON-SITE ASSISTANCE

    - Occupancy Adjustments: Within one year of date of Substantial Completion, provide up to three Project site visits, when requested, to adjust light levels, make preset scene changes, and adjust controls to suit actual conditions.

    - For occupancy and motion sensors, verify operation at outer limits of detector range. Set time delay to suit Owner's operations.

    - For daylighting controls, adjust set points and deadband controls to suit Owner's operations.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions