READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Fuses” Work is shown in the Contract Documents.  This section includes cartridge fuses, rated 600V and less, for use in switches, panelboards, switchboards, controllers, and motor-control centers; and spare fuse cabinets.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - NEMA FU 1 (National Electrical Manufacturers Association) - Low Voltage Cartridge Fuses,

    - NFPA 70 (National Fire Protection Association) - National Electrical Code,

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: Include the following for each fuse type indicated:

        - Ambient Temperature Adjustment Information: If rating of fuses has been adjusted to accommodate ambient temperatures, provide list of fuses with adjusted ratings.

          - For each fuse having adjusted ratings, include location of fuse, original fuse rating, local ambient temperature and adjusted fuse rating.

          - Provide manufacturer’s technical data on which ambient temperature adjustment calculations are based.

        - Dimensions and manufacturer’s technical data on features, performance, electrical characteristics, and ratings.

        - Let-through current curves for fuses with current-limiting characteristics.

        - Time-current coordination curves and current-limitation curves for each type and rating of fuse. Coordination charts and tables, and related data.

        - Fuse size for elevator feeders and elevator disconnect switches.

  - QUALITY ASSURANCE

    - Source Limitations: Provide fuses from a single manufacturer.

    - On low-voltage systems, provide nonrenewable cartridge fuses, class and current rating required, voltage rating consistent with circuit voltage.

    - Listing and Labeling: Provide components, devices and accessories that are Listed and Labeled as defined in NFPA 70, Article 100 and marked for intended use for the location and environment in which they are installed.

    - Comply with NEMA FU 1.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

  - COORDINATION

    - Coordinate fuse ratings with HVAC and refrigeration equipment nameplate limitations of maximum fuse size.

    - Select fuses to provide appropriate levels of short circuit and overcurrent protection for components such as wire and cable, bus structures, and other overcurrent equipment.

    - Select fuses to coordinate with time-current characteristics of other overcurrent protective elements, such as other fuses, circuit breakers, and protective relays. Design system to ensure that device closest to fault operates first.

    - The Engineer shall verify that the let-through current of the selected fuse does not exceed the rating of downstream devices or conductors. The Engineer shall calculate the short-circuit capability of downstream cable to verify that it is protected by the fuse time-current characteristic curve.

    - The Engineer shall selectively coordinate all protective devices so faults are isolated to the most localized level.

      - On low voltage systems this may occasionally indicate the use of a fuse in series with a circuit breaker.

      - On medium voltage systems, particular care should be given to coordination of padmount vacuum fault interrupters with upstream feeder fuses and coordination of fuses in series through a transformer (i.e. a 12.47-4.12kV transformer with primary and secondary fuses).

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided.  Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Fuses: [3] of each fuse type and size

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Bussmann; Division of Cooper Industries.

      - Ferraz Shawmut.

      - Littelfuse.

      - Or Approved Equal.

  - CARTRIDGE FUSES

    - Characteristics: NEMA FU 1, non-renewable cartridge fuse; class and current rating indicated; voltage rating consistent with circuit voltage.

  - LOW-VOLTAGE FUSES

    - Fuses for circuits under 600V shall be UL listed, Class J, Class L, Class R or RK.

    - Fuses for safety switches shall be class R, intended for use with rejection clips.

      - Use Class L and Class T fuses to protect loads over 600 Amps such as transformer secondaries, switchboard mains or large feeders

      - Use Class J, Class K and Class R fuses to protect most feeder and branch-circuit applications.

    - Fuse Applications:

      - Main Services and Main Feeders

        - 601 to 6000A circuits:  Provide Class L with 4-second minimum time delay at 500% rated current, with an interrupting rating of 200,000 amperes RMS symmetrical.

        - 600 amperes and less circuits:  Provide Class RK1 dual-element, time-delay, non-interchangeable fuses with an interrupting rating of 200,000 amperes, for 600 volt and 250-volt applications, respectively.

        - 600-volt RK1 fuses shall have an indicating feature, which clearly indicates when fuse is opened (blown).

      - Motor Circuit Fuses:  Provide Class RK1 and Class J dual-element time-delay fuses with 10-second minimum time delay at 500% rated current, sized at 125% of full-load current of motor.

      - Current limiting fuses Protecting Molded-Case Circuit Breaker Panelboards

        - Molded case circuit breaker panelboards, having short-circuit ratings less than the available short-circuit current at the point where the panelboard is applied, shall be protected by Class and maximum fuse ratings listed by the panelboard manufacturer.

        - Class G (300V) and Class CC (600V) current limiting, noninterchangeable, time delay or non-time delay fuses are used in branch-circuit panelboards.

      - Lighting Fixture Protection

        - Lighting fixture ballasts shall be individually protected on their line.

        - In each instance, fuse size and type shall be as recommended by the fixture or ballast manufacturer.

  - MEDIUM-VOLTAGE FUSES

    - Fuses for medium-voltage motors shall be R-rated for use with an overload relay and contactor as part of a medium-voltage motor starter package.  Typically, the starter manufacturer will select the fuse.

    - Fuses for other medium-voltage loads including transformers, feeders, and capacitors shall be E-rated general-purpose current limiting fuses.

  - POTENTIAL TRANSFORMER FUSES

    - Medium-voltage fuses shall be E-Rated, intended for the purpose.  Low-voltage fuses shall be as selected by the original equipment manufacturer.

  - SPARE FUSE CABINET

    - Cabinet: Wall-mounted, 0.05-inch- thick steel unit with full-length, recessed piano-hinged door and key-coded cam lock and pull.

      - Size: Adequate for storage of spare fuses specified with 15 percent spare capacity minimum.

      - Finish: Gray, baked enamel.

      - Identification: “SPARE FUSES” in 1-1/2-inch high letters on exterior of door.

      - Fuse Pullers: For each size fuse.

- EXECUTION

  - EXAMINATION

    - Examine fuses before installation. Reject fuses that are moisture damaged or physically damaged.

    - Examine holders to receive fuses for compliance with installation tolerances and other conditions affecting performance, such as rejection features.

    - Examine utilization equipment nameplates and installation instructions. Install fuses of sizes and with characteristics appropriate for each piece of equipment.

    - Evaluate ambient temperatures to determine if fuse rating adjustment factors must be applied to fuse ratings.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - FUSE APPLICATIONS

    - Main Services and Main Feeders:

      - 601A to 6000A circuits: Class L, minimum 4 second time delay at 500% rated current, with an interrupting rating of 200,000 amperes RMS symmetrical.

      - 600A and less circuits: Class RK1 dual-element, time delay, non-interchangeable fuses with an interrupting rating of 200,000 amperes, for 600V and 250V applications.

        - 600V RK1 fuses shall have an indicating feature which clearly indicates when fuse is opened (blown).

    - Motor Branch Circuits: Class RK1 and Class J dual element time-delay fuses with 10-second minimum time delay at 500% rated current, sized at 125% of full load current of motor.

    - Current Limiting Fuses Protecting Molded Case Circuit Breaker Panelboards:

      - Molded case circuit breaker panelboards having short circuit ratings less than the available short circuit current at the point where the panelboard is applied shall be protected by Class and maximum fuse ratings listed by the panelboard manufacturer.

      - Class G (300V) and Class CC (600V) current limiting, non-interchangeable time delay or non-time delay fuses are used in branch circuit panelboards.

    - Light Fixture Protection:

      - Luminaire ballasts shall be individually protected on their line.

      - In each instance, fuse size and type shall be as recommended by the fixture or ballast manufacturer.

  - FUSE INSTALLATION

    - Install fuses in fusible devices. Arrange fuses so that manufacturer, type and rating information is readable without removing fuse. Do not mix brands of types of fuses in device.

    - The Electrical Contractor at the job site shall install all fuses only when equipment is to be energized. Fuses shall not be installed prior to shipment.

    - Install spare fuse cabinet[s].

  - IDENTIFICATION

    - Install labels indicating fuse replacement information on inside door of each fused switch as specified in Section 26 05 53 - Electrical Identification.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Changed Specification Section Number