READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Mechanical Sound, Vibration and Seismic Control” Work is shown in the Contract Documents.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - ASA (Acoustical Society of America)

      - ARI (Air Conditioning and Refrigeration Institute)

      - AMCA (Air Movement and Control Association)

      - ANSI (American National Standards Institute)

      - ASHRAE (American Society of Heating, Refrigerating and Air Conditioning Engineers)

      - ASTM (American Society for Testing and Materials)

      - SMACNA (Sheet Metal and Air Conditioning Contractors’ National Association)

      - IBC (International Building Code)

      - ICC-ES (ICC-Evaluation Service)

  - PERFORMANCE REQUIREMENTS

Use this article carefully; restrict statements to identify system performance requirements or function criteria only.

Seismic design shall be initiated as required and calculations shall be submitted for review, generated by a Professional Engineer, licensed in the State of Washington for this type of Work.

    - Provide vibration isolation on motor driven equipment over 0.5 hp, plus connected piping and ductwork.

    - Provide minimum static deflection of isolators for equipment as indicated.

      - Basement, Under 20 hp

        - Under 400 rpm: [___]

        - 400 - 600 rpm: 1 inch

        - 600 - 800 rpm: 0.5 inch

        - 800 - 900 rpm: 0.2 inch

        - 1100 - 1500 rpm: 0.14 inch

        - Over 1500 rpm: 0.1 inch

      - Basement, Over 20 hp

        - Under 400 rpm: [___]

        - 400 - 600 rpm: 2 inch

        - 600 - 800 rpm: 1 inch

        - 800 - 900 rpm: 0.5 inch

        - 1100 - 1500 rpm:0.2 inch

        - Over 1500 rpm: 0.15 inch

      - Upper Floors, Normal

        - Under 400 rpm: [___]

        - 400 - 600 rpm: 3.5 inch

        - 600 - 800 rpm: 2 inch

        - 800 - 900 rpm: 1 inch

        - 1100 - 1500 rpm: 0.5 inch

        - Over 1500 rpm: 0.2 inch

      - Upper Floors, Critical

        - Under 400 rpm: [___]

        - 400 - 600 rpm: [___]

        - 600 - 800 rpm: 3.5 inch

        - 800 - 900 rpm: 2 inch

        - 1100 - 1500 rpm: 1 inch

        - Over 1500 rpm: 0.5 inch

    - Consider upper floor locations critical unless otherwise indicated.

    - Use concrete inertia bases for fans having static pressure in excess of 3.5 inch wc or motors in excess of 40 hp, and on base mounted pumps over 10 hp.

    - Maintain sound level of spaces at levels not to exceed those listed below by utilizing acoustical devices.

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall be as follows:

      - Shop Drawings: Indicate inertia bases and locate vibration isolators, with static and dynamic load on each. Indicate assembly, materials, thickness, dimensional data, pressure losses, acoustical performance, layout, and connection details for sound attenuation products fabricated for this project.

      - Product Data: Submit schedule of vibration isolator type with location and load on each. Provide catalog information indicating, materials, dimensional data, pressure losses, and acoustical performance for standard sound attenuation products.

      - Design Data: Provide engineering calculations maximum room sound levels are not exceeded.

      - Test Reports: Indicate [dynamic insertion loss and noise generation values of silencers] [acoustic housings meet or exceed specified sound transmission loss values].

      - Manufacturer's Installation Instructions: Submit special procedures and setting dimensions. Indicate installation requirements that maintain integrity of sound isolation.

      - Manufacturer's Certificate: Certify that isolators meet or exceed specified requirements.

      - Manufacturer's Field Reports: Indicate [sound] isolation installation is complete and in accordance with instructions.

  - CLOSEOUT SUBMITTALS

    - Project Record Documents: Record actual locations of [cross-talk silencers] [acoustic housings] [ductwork lagging]. Record actual locations of hangers including attachment points.

  - QUALITY ASSURANCE

    - Perform Work in accordance with [AMCA 300] [ANSI S1.13] [ARI 575] [ASA 16] [ANSI S1.36] standards and recommendations of [ASHRAE 68].

Include the following paragraph only when the costs of acquiring the specified standards are justified

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years [documented] experience.

    - Installer: Company specializing in performing Work of this section with minimum three years [documented] experience [approved by manufacturer].

    - Design application of [duct silencers] [acoustic housings] [seismic snubbers] under direct supervision of a Professional Engineer experienced in design of this Work and licensed in the State of Washington.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

Edit the following descriptive specifications to identify Project requirements.

  - INERTIA BASES

    - Structural Bases:

      - Design: Sufficiently rigid to prevent misalignment or undue stress on machine, and to transmit design loads to isolators and snubbers.

      - Construction: Welded structural steel with gusset brackets, supporting equipment and motor with motor slide rails.

    - Concrete Inertia Bases:

      - Mass: Minimum of 1.5 times weight of isolated equipment.

      - Construction: Structured steel channel perimeter frame, with gusset brackets and anchor bolts, adequately reinforced, concrete filled.

      - Connecting Point: Reinforced to connect isolators and snubbers to base.

      - Concrete: Reinforced 3,000 psi concrete.

  - VIBRATION ISOLATORS

Edit the following descriptive specifications to identify Project requirements.

    - Manufacturers: Amber Booth, Kinetics, Mason Industries, Or Approved Equal.

    - Open Spring Isolators:

      - Spring Isolators:

        - For Exterior and Humid Areas: Provide hot dipped galvanized housings and neoprene coated springs.

        - Code: Color code springs for load carrying capacity.

      - Springs: Minimum horizontal stiffness equal to 75 percent vertical stiffness, with working deflection between 0.3 and 0.6 of maximum deflection.

      - Spring Mounts: Provide with leveling devices, minimum 0.25 inch thick neoprene sound pads, and zinc chromate plated hardware.

      - Sound Pads: Size for minimum deflection of 0.05 inch; meet requirements for neoprene pad isolators.

    - Restrained Spring Isolators:

      - Spring Isolators:

        - For Exterior and Humid Areas: Provide hot dipped galvanized housings and neoprene coated springs.

        - Code: Color code springs for load carrying capacity.

      - Springs: Minimum horizontal stiffness equal to 75 percent vertical stiffness, with working deflection between 0.3 and 0.6 of maximum deflection.

      - Spring Mounts: Provide with leveling devices, minimum 0.25 inch thick neoprene sound pads, and zinc chromate plated hardware.

      - Sound Pads: Size for minimum deflection of 0.05 inch; meet requirements for neoprene pad isolators.

      - Restraint: Provide heavy mounting frame and limit stops.

    - Closed Spring Isolators:

      - Spring Isolators:

        - For Exterior and Humid Areas: Provide hot dipped galvanized housings and neoprene coated springs.

        - Code: Color code springs for load carrying capacity.

      - Type: Closed spring mount with top and bottom housing separated with neoprene rubber stabilizers.

      - Springs: Minimum horizontal stiffness equal to 75 percent vertical stiffness, with working deflection between 0.3 and 0.6 of maximum deflection.

      - Housings: Incorporate neoprene isolation pad meeting requirements for neoprene pad isolators, and neoprene side stabilizers with minimum 0.25 inch clearance.

    - Restrained Closed Spring Isolators:

      - Spring Isolators:

        - For Exterior and Humid Areas: Provide hot dipped galvanized housings and neoprene coated springs.

        - Code: Color code springs for load carrying capacity.

      - Type: Closed spring mount with top and bottom housing separated with neoprene rubber stabilizers.

      - Springs: Minimum horizontal stiffness equal to 75 percent vertical stiffness, with working deflection between 0.3 and 0.6 of maximum deflection.

      - Housings: Incorporate neoprene isolation pad meeting requirements for neoprene pad isolators, and neoprene side stabilizers with minimum 0.25 inch clearance and limit stops.

    - Spring Hanger:

      - Spring Isolators:

        - For Exterior and Humid Areas: Provide hot dipped galvanized housings and neoprene coated springs.

        - Code: Color code springs for load carrying capacity.

      - Springs: Minimum horizontal stiffness equal to 75 percent vertical stiffness, with working deflection between 0.3 and 0.6 of maximum deflection.

      - Housings: Incorporate [neoprene isolation pad meeting requirements for neoprene pad isolators] [rubber hanger with threaded insert].

      - Misalignment: Capable of 20 degree hanger rod misalignment.

    - Neoprene Pad Isolators:

      - Rubber or neoprene-waffle pads.

        - 30 durometer.

        - Minimum 1/2 inch thick.

        - Maximum loading 40 psi.

        - Height of ribs shall not exceed 0.7 times width.

      - Configuration: [Single layer] [1/2 inch thick waffle pads bonded each side of 1/4 inch thick steel plate]

    - Rubber Mount or Hanger: Molded rubber designed for 0.5 inches deflection with threaded insert.

    - Glass Fiber Pads: Neoprene jacketed pre-compressed molded glass fiber.

    - Seismic Snubbers:

      - Type: Non-directional and double acting unit consisting of interlocking steel members restrained by neoprene elements.

      - Neoprene Elements: Replaceable, minimum of 0.75 inch thick.

      - Capacity: 4 times load assigned to mount groupings at 0.4 inch deflection.

      - Attachment Points and Fasteners: Capable of withstanding 3 times rated load capacity of seismic snubber.

  - DUCT SILENCERS

Edit the following descriptive specifications to identify Project requirements.

    - Description: Duct section with sheet metal outer casing, sound absorbing fill material, and inner casing of perforated sheet metal; incorporating interior baffles of similar construction. Fabricate in accordance with SMACNA HVAC Duct Construction Standards - Metal and Flexible.

    - Configuration: Tubular [with] [without] inner casing and liner, [without center body] [with absorptive] [aerodynamically shaped center body with nose cone and truncated tail cone] [splitters with radius nose and contoured tails], [___] diameter [as indicated], length [1.5] [2] [3] [4] times diameter.

OR

    - Configuration: Rectangular with lined splitters with radius nose and contoured tails, modular [___] high, [___] wide, [___] long.

    - Materials:

      - Outer Casing: Minimum [22 gage] [20 gage] thick galvanized steel stiffened as required, with [mastic filled lock formed] [welded] seams, 2 inch long,11 gage slip joints on both ends.

      - Inner Casing and Splitters: Minimum 24 gage thick perforated galvanized steel.

      - Fill: Glass fiber or mineral wool of minimum [4 lb/cu ft] [3 lb/cu ft] density.

      - Fill Liner: [Bonded glass fiber matting] [1 mil Mylar film].

    - Rating:

      - ASTM E477 Insertion Loss and Maximum Generated Noise at [1000 fpm] [2000 fpm] [4000 fpm] Face Velocity:

        - Octave Band Center Frequency (Hz) 63, 125, 250, 500, 1000, 2000, 4000

        - Insertion Loss (dB) [___], [___], [___], [___], [___], [___], [___]

        - Generated Noise (dB) [___], [___], [___], [___], [___], [___], [___]

      - Static Pressure Drop at [1000 fpm] [2000 fpm] Face Velocity: [___] inches wg.

      - Air Tight Static Pressure: [10 inches wg].

    - Performance: Achieve noise reduction of:

      - Octave Band Center Frequency (Hz) 63, 125, 250, 500, 1000, 2000, 4000

      - Insertion Loss (dB) [___], [___], [___], [___], [___], [___], [___]

  - CROSS-TALK SILENCERS

Edit the following descriptive specifications to identify Project requirements.

    - Description: Duct sections with sheet metal outer casing, sound absorbing fill material [and inner casing of perforated sheet metal]; incorporating interior baffles of similar construction. Fabricate in accordance with SMACNA HVAC Duct Construction Standards - Metal and Flexible.

    - Configuration: Rectangular, lined [with inner casing] with splitters with radius nosed and contoured tails, [___] high, [___] wide, [___] long.

    - Materials:

      - Outer Casing: Minimum [22 gage] thick galvanized steel with [mastic filled lock formed] [welded] seams, 3 inch long and 11 gage slip joint on both ends.

      - Inner Casing and Splitters: Minimum 24 gage thick perforated galvanized steel.

      - Fill: Glass fiber or mineral wool of minimum [4 lb/cu ft] [3 lb/cu ft] density.

      - Fill Liner: [Bonded glass fiber matting] [1 mil Mylar film].

    - Rating:

      - Equivalent STC: [___]

      - Static Pressure Drop at [500 fpm] [100fpm] Face Velocity: [___] inches wg.

  - ACOUSTIC HOUSINGS

Edit the following descriptive specifications to identify Project requirements.

    - Description: Modular panels, including access doors and windows, nominal 4 inches thick, with filled outer and inner casing. Fabricate and support in accordance with SMACNA HVAC Duct Construction Standards - Metal and Flexible.

    - Materials:

      - Outer Casing: Minimum [18 gage] [22 gage] thick galvanized steel stiffened as required, with [mastic filled lock formed] [welded] seams for [internal flange butt] [covering strip butt] [overlapping lip] [tongue and groove] joining.

      - Inner Casing and Splitters: Minimum 22 gage thick perforated galvanized steel.

      - Fill: Glass fiber or mineral wool of minimum [4 lb/cu ft] [4-3/4 lb/cu ft] density.

      - Fill Liner: [Bonded glass fiber matting] [1 mil Mylar film].

      - Window: [___] x [___] inch double glazed with 1/4 inch safety glass.

    - Rating: ASTM E90 sound transmission loss minimum:

      - Octave Band Center Frequency (Hz) 63, 125, 250, 500, 1000, 2000, 4000

      - Transmission Loss (dB) [___], [___], [___], [___], [___], [___], [___]

    - Performance: ASTM E596, achieve A Scale noise reduction of:

      - Octave Band Center Frequency (Hz) 63, 125, 250, 500, 1000, 2000, 4000

      - Insertion Loss (dB) [___], [___], [___], [___], [___], [___], [___]

  - DUCTWORK LAGGING

    - Acoustic Insulation: [2 inch] [___] thick, 3 to 5 lb/cu ft density glass fiber or mineral wool insulation.

    - Covering: [Sheet lead] [plaster] [or] [gypsum board] with surface weight minimum 4 lb/sq ft.

  - ACOUSTICAL LOUVERS

Note to Engineer: Edit the following descriptive specifications to identify Project requirements.

    - Acoustic Louvers: As specified in Section 10210 - Wall Louvers.

OR

    - Configuration: [8] [12] [___] inch deep louvers with blades on 45 degree slope; sound absorbing fill material, and inner surface of perforated sheet metal, heavy channel frame, bird Screen.

    - Materials:

      - Louvers: [16 gage galvanized steel] [or] [12 gage extruded aluminum], welded assembly, with factory [prime coat] [baked enamel] [color anodized] finish.

      - Inner Surface: Minimum 24 gage thick perforated galvanized steel.

      - Fill: Glass fiber or mineral wool of minimum [4 lb/cu ft] [3 lb/cu ft] density.

      - Fill Liner: [Bonded glass fiber matting] [1 mil Mylar film].

      - Bird screen: [1] [1/2] [3/4] inch square wire mesh.

      - Mounting: [Interior] [Exterior] [flat flange] [angle flange] [Screw holes in jambs] [Masonry strap anchors].

    - Rating:

      - Insertion loss:

        - Octave Band Center Frequency (Hz) 63, 125, 250, 500, 1000, 2000, 4000

        - Insertion Loss (dB) [___], [___], [___], [___], [___], [___], [___]

      - Static Pressure Drop at [200 fpm] [300 fpm] [400 fpm] Face Velocity: [___] inches wg.

- EXECUTION

  - EXAMINATION

    - Verify that all equipment, ductwork and piping that is installed before Work in this section begins is as shown on the Project drawings.

  - EXISTING WORK

    - Ensure access to existing piping and ductwork and other installations which remain active and which require access. Modify installation or provide access panel as appropriate.

    - Extend existing piping and ductwork installations using materials and methods [compatible with existing electrical installations, or] as specified.

  - INSTALLATION

    - Support duct silencers [independent of] [rigidly to] ductwork. [With flexible duct connections, lagged with leaded vinyl sheet on inlet and outlet]

    - Install cross-talk silencers in wall. Caulk wall penetrations.

    - Lag ductwork, where indicated by wrapping with insulation and covering. Apply covering to be airtight. Do not attach covering rigidly to ductwork.

    - Attach ductwork to acoustic louvers with flexible duct connections.

    - Install isolation for motor driven equipment.

      - Bases:

      - Set steel bases for 1 inch clearance between housekeeping pad and base.

      - Set concrete inertia bases for 2 inch clearance between housekeeping pad and base.

      - Adjust equipment level.

    - Install spring hangers without binding.

    - On closed spring isolators, adjust so side stabilizers are clear under normal operating conditions.

    - Prior to making piping connections to equipment with operating weights substantially different from installed weights, block up equipment with temporary shims to final height. When full load is applied, adjust isolators to load to allow shim removal.

    - Provide pairs of horizontal limit springs on fans with more than [6.0] [___] inch static pressure, and on hanger supported, horizontally mounted axial fans.

In earthquake areas provide seismic snubbers.  Ensure proven systems are used.

    - Provide resiliently mounted equipment, piping, and ductwork with seismic snubbers. Each inertia base shall have minimum of four seismic snubbers located close to isolators. Snub equipment designated for post disaster use to 0.05 inch maximum clearance. Other snubbers shall have clearance between 0.15 inch and 0.25 inch.

    - Support piping connections to isolated equipment resiliently [for scheduled distance] [to nearest flexible pipe connector] [as follows:]

      - Up to 4 inch Diameter: First three points of support.

      - 5 to 8 inch Diameter: First four points of support.

      - 10 inch Diameter and Over: First six points of support.

      - Select three hangers closest to vibration source for minimum 1.0 inch static deflection or static deflection of isolated equipment. Select remaining isolators for minimum 1.0 inch static deflection or 1/2 static deflection of isolated equipment.

    - Connect wiring to isolated equipment with flexible hanging loop.

  - FIELD QUALITY CONTROL

    - Inspect isolated equipment after installation and submit report. Include static deflections.

    - After start-up, final corrections and balancing of systems take octave band sound measurements over full audio frequency range in areas adjacent to mechanical equipment rooms, duct and pipe shafts, and other critical locations, as directed. Provide one-third octave band measurements of artificial sound sources in areas indicated as having critical requirements. Submit complete report of test results including sound curves.

  - MANUFACTURER'S FIELD SERVICES

    - Provide services of testing agency to take noise measurement. Use meters meeting requirements of ASA 47 (ANSI S1.4).

  - SCHEDULES

Provide a schedule when there is more than one of each size unit.  3.07	Refer to Port of Seattle Aviation/Facilities and Infrastructure “Mechanical Systems Standards, January 22, 2014”.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions