READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure Standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Fire Pump” Work is shown in the Contract Documents. Section includes fire pump package, fire pump, [motor] [engine], electric jockey pump, and controllers.

  - GOVERNING CODES, STANDARDS, AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - FM (Factory Mutual System) - Approval Guide.

    - NEMA MG-1 (National Electrical Manufacturers Association) - Motors and Generators.

    - NEMA 250 (National Electrical Manufacturers Association) - Enclosures for Electrical Equipment (1000 Volt Maximum).

    - NFPA

    - NFPA 13 (National Fire Protection Association) - Installation of Sprinkler Systems.

    - NFPA 20 (National Fire Protection Association) - Installation of Centrifugal Fire Pumps.

    - NFPA 20 fire pump

    - NFPA 20 flow test

    - NFPA 37 (National Fire Protection Association) - Installation and Use of Stationary Combustion Engines and Gas Turbines.

    - NFPA 37 diesel engine drive

    - NFPA 1247

    - UL (Underwriters Laboratories, Inc.) - Fire Protection Equipment Directory.

    - UL 448 (Underwriters Laboratories, Inc.) - Pumps for Fire Protection Service.

    - UL 778 (Underwriters Laboratories, Inc.) - Motor Operated Water Pumps.

    - UL 1247 (Underwriters Laboratories, Inc.) - Diesel Engines for Driving Centrifugal Fire Pumps.

    - UL 1478 (Underwriters Laboratories, Inc.) - Fire Pump Relief Valves.

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Shop Drawings: Indicate layout, general assembly, components, dimensions, weights, clearances, and methods of assembly.

      - Product Data: Submit manufacturers literature including general assembly, pump curves showing performance characteristics with pump and system, operating point indicated, NPSH curve, controls, wiring diagrams, and service connections.

      - Field Test Reports: Indicate results of hydrostatic test and field acceptance tests.

      - Manufacturer's Installation Instructions: Submit support details, connection requirements, for fire pump system.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

  - DESIGN REQUIREMENTS

Use this article carefully; restrict statements to identify system design requirements only.

    - Conform to NFPA 20.

  - QUALITY ASSURANCE

    - Perform Work in accordance with [UL Fire Protection Equipment Directory] [FM Approval Guide] [Warnock Hersey] [State of Washington] [City of SeaTac] [City of Seattle] standard.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years [documented] experience [and with service facilities within (100) (___) miles of Project].

    - Installer: Company specializing in performing Work of this section with minimum three years [documented] experience [approved by manufacturer].

    - Design fire pump system under direct supervision of a Professional Engineer experienced in design of this Work and licensed in the State of Washington.

  - DELIVERY, STORAGE, AND HANDLING

Identify any special delivery, storage or handling requirements.

    - Accept fire pumps and components on site in factory packing. Inspect for damage. Comply with manufacturers rigging and installation instructions.

    - Protect fire pumps and components from physical damage including effects of weather, water, and construction debris.

    - Provide temporary, inlet and outlet caps and maintain in place until installation.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

  - MAINTENANCE SERVICE

    - Provide service and maintenance of fire pump, driver, and controller for [five] year from Date of Substantial Completion.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Supply [one] set of [gaskets] [screens] [seals] [___] for each pump type and model supplied

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - FIRE PUMPS

    - Perform Work in accordance with [UL Fire Protection Equipment Directory] [FM Approval Guide] [Warnock Hersey] [State of Washington] [City of SeaTac] [City of Seattle] standard.

Edit the following descriptive specifications to identify Project requirements and to eliminate any conflict with manufacturers specified above.

  - VERTICAL IN-LINE PUMPS

    - Type: UL 448 [and UL 778], vertical, single stage, close coupled, radial [or horizontally] split casing, for in-line mounting, for 250 psi.

    - Casting: Cast or ductile iron, with suction and discharge gage port, casing wear ring, seal flush connection, drain plug, flanged suction and discharge.

    - Impeller: Bronze, fully enclosed, keyed directly to motor shaft.

    - Shaft: Solid alloy steel with bronze sleeve.

Select one of the following two paragraphs for seal type desired. Packing gland seals are required for UL listed and labeled pumps.

    - Seal: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings, 230 degrees F maximum continuous operating temperature.

OR

    - Seal: Carbon rotating against a stationary ceramic seat  with a seal suitable for [225 degrees F] maximum continuous operating temperature.

Use the following paragraph for one or more identical pumps. Use a pump schedule when specifying pumps with different criteria.

    - Performance: Flow: [___] gpm, at [___] feet head.

  - HORIZONTAL BASE MOUNTED PUMPS

    - Type: UL 448 [and UL 778], horizontal shaft, single stage, double suction, direct connected, horizontally split casing, for 250 psi maximum working pressure.

    - Casing: Cast iron, with suction and discharge gage ports, renewable bronze casing wearing rings, seal flush connection, drain plug, flanged suction and discharge.

    - Impeller: Bronze double suction fully enclosed, balanced and keyed to shaft.

    - Bearings: Grease lubricated ball bearings, replaceable without opening casing.

    - Shaft: Alloy steel with replaceable bronze shaft sleeve.

    - Seal: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings, 230 degrees F maximum continuous operating temperature.

    - Drive: Flexible coupling with coupling guard.

    - Base plate: Cast iron [or fabricated steel] with integral drain rim.

Use the following paragraph for one or more identical pumps. Use a pump schedule when specifying pumps with different criteria.

    - Performance: Flow [___] gpm, at [___] feet head.

  - VERTICAL TURBINE PUMPS

    - Type: UL 448 [and UL 778] vertical, centrifugal, turbine.

    - Casing: Cast iron, rated for 250 psi or 1.20 times actual discharge working pressure discharge gage, air vent, wear rings, seal flush connection, drain plug, and flanged discharge.

    - Impellers: Bronze, fully enclosed, keyed to shaft or secured with lock nut.

    - Shaft: Stainless steel or carbon steel with bronze or stainless steel sleeve through seal chamber.

    - Seals: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings.

Use the following two paragraphs for one or more identical pumps. Use the pump schedule when specifying pumps with different criteria.

    - Performance: Flow [___] gpm, at [___] feet head.

  - FIRE PUMP ACCESSORIES

Select applicable accessories. All are not appropriate to all types of pumps and systems.

    - Eccentric suction reducer and OS&Y gate or butterfly valve on suction side of pump.

    - Concentric increaser and check valve in pump discharge and butterfly valve on system side of check valve.

    - Fire pump bypass fitted with butterfly valves and check valve.

    - Main relief-valve, UL 1478, [and (enclosed/open) type waste cone].

    - Suction pressure gage, 4 1/2 inch diameter dial with snubber, valve cock and lever handle.

    - Discharge pressure gage mounted on board attached to pump, with snubber, valve cock and lever handle.

    - Casing 3/4 inch relief valve.

    - Float operated [3/4 inch] [1 inch] automatic air release valve.

    - Hose valve manifold with 2-1/2 inch hose gate valves with caps and chains.

In some jurisdictions, the following paragraph is permitted instead of manifold note above.

    - Flow metering system for closed loop testing.

  - ELECTRIC MOTOR DRIVE

    - Motor: Squirrel cage induction type; in open drip proof NEMA MG-1 enclosure, [3500] [1750] rpm.

    - Controller: Limited service type with [auto-transformer] [primary resistor] [reduced voltage] [part winding] [across-the-line] starter, in NEMA 250 enclosure, including the following:

      - Disconnect Switch: Externally operable, quick break type.

      - Circuit Breaker: Size to NFPA 20, minimum 65,000 amperes interrupting capacity.

      - Motor Starter: Energized automatically through pressure switch or manually by externally operable handle.

      - Pressure Switch: Set to cut in at [___] psi.

      - Running Period Timer: Keeps motor in operation when started automatically, for a minimum of seven minutes.

      - Pilot Lamp: Indicates circuit breaker closed and power available.

      - Test Accessories: Ammeter test link and voltmeter test studs.

      - Alarm Relay: Energizes alarm to indicate circuit breaker open or power failure.

      - Switch Relay: For remote start.

      - Manual Selector Station: On enclosure marked "Automatic" and "Non-Automatic."

  - DIESEL ENGINE DRIVE

    - Diesel Engine: Conform to NFPA 1247, arranged for automatic operation and include overspeed/overcrank switch and drive, two contactor switches, low oil pressure and high water temperature warning switches, and fuel shut-off solenoid, with wiring terminating in junction box.

    - Include following engine accessories:

      - Stub shaft.

      - Oil bath air cleaner.

      - Water-cooled exhaust manifold.

      - Heat exchanger.

      - Mechanical speed governor.

      - Fuel filter.

      - Lube oil filter and by-pass valve.

      - Lube oil cooler and relief valve.

      - Fuel pump.

      - Instrument panel with tachometer, hour meter, oil pressure gage, water-temperature gage, ammeter, hand speed control and start switch.

      - Starting system including generator/alternator, starting-motor and voltage regulator.

      - Exhaust silencer, residential type.

      - Flexible exhaust tubing, [24 inches] long.

    - Cooling water system: Closed system with cooling water supply to heat exchanger from fire pump discharge. Include four (4) manual shut-off valves (including by-pass line), two strainers, pressure regulating valve, automatic solenoid valve and pressure gage.

    - Storage batteries: Dual lead acid batteries with cables and battery racks.

    - Fuel system: [___] gal above ground storage tank, fill pipe and cap, manual shut-off valve, flame-arrestor, oil level gage, braided bronze flexible connectors, seamless type L copper tubing with flared joints. Fill tank at completion.

    - Automatic diesel engine controller: Enclosed in floor mounted [14 gage] steel housing, UL listed and labeled.

      - Controller: Function to automatically start fire pump from water pressure control switch or test switch.

      - Stop push button: To manually stop engine.

      - Automatic conditions: Controller shall alternate batteries automatically on each 15 second cranking cycle. Alarm if engine not started after six attempts.

      - Battery charger: Dual, built-in, to recharge both batteries within 24-hour period, with automatic overload protection (current limiting), individual voltmeters and ammeters for each battery.

      - Individual pilot lights and common alarm bell for:

        - Charger 1 Failure

        - Charger 2 Failure

        - Battery 1 Failure

        - Battery 2 Failure

        - AC Power On

        - Exercise Cycle

        - High Engine Jacket Water Temperature

        - Low Engine Oil Pressure

        - Engine Failure to Start Automatically

        - Overspeed Shutdown

        - Engine Run

        - Main Switch in Auto

        - Low Fuel Level

        - Low Water Reservoir Level

        - Water Reservoir Empty

        - Low Pump Room Temperature

        - Low Suction Temperature

        - Flow Meter On

        - Relief Valve Open

  - PRESSURE BOOSTER (JOCKEY) PUMP

    - Perform Work in accordance with [UL Fire Protection Equipment Directory] [FM Approval Guide] [Warnock Hersey] [State of Washington] [City of SeaTac] [City of Seattle] standard.

Edit the following descriptive specifications to identify Project requirements and to eliminate any conflict with manufacturers specified above.

    - Electrically operated horizontal [turbine] [close-coupled] type with standard open drip-proof horizontal motor.

    - Control by automatic jockey pump controller with full voltage starter [and minimum run timer] to start pump on pressure drop in system [and stay in operation for minimum period of time]. Fire pump shall start automatically on further pressure drop or on jockey pump failure.

  - ELECTRICAL CHARACTERISTICS AND COMPONENTS

Select one or more of the following subparagraphs appropriate to the equipment requirements.

    - Section 26 27 26 - Wiring Devices: Requirements for electrical characteristics.

      - [___ hp] [___ W] [___] rated load amperes.]

      - [___ volts], [single] [three] phase, 60 Hz.

      - [___] amperes maximum [fuse size] [circuit breaker size] [over current protection].

      - [___] minimum circuit ampacity.

      - [___] percent minimum power factor at rated load.

    - Disconnect Switch: Factory mount [in control panel] [on equipment].

- EXECUTION

  - INSTALLATION

    - Install Fire Pump in accordance with NFPA 20 and Diesel Engine Drive in accordance with NFPA 37

OR

    - Perform Work in accordance with [UL Fire Protection Equipment Directory] [FM Approval Guide] [Warnock Hersey] [State of Washington] [City of SeaTac] [City of Seattle] standard.

    - Provide access space around pumps for service; no less than minimum as recommended by manufacturer.

    - Install fire suppression piping in accordance with these Specifications. Decrease from line size with long radius reducing elbows or reducers. Support piping adjacent to pump such that no weight is carried on pump casings. For base mounted pumps, provide supports under elbows on pump suction and discharge.

    - Provide drains for bases and seals, piped to and discharging into floor drains.

    - Mount unit on vibration isolators. Refer to Section 20 05 48 - Mechanical Sound, Vibration, and Seismic Control.

    - Provide piping for fuel supply and return connected to motor. Provide piping to and from exhaust silencer with thimble at wall or roof penetrations.

    - Insulate piping associated with pump, pump casing and exhaust silencer. Refer to Section 20 07 00 - Mechanical Insulation.

    - Connect to electrical service. Refer to Section 26 27 26 - Wiring Devices.

    - Lubricate pumps before start-up.

    - Check, align, and certify base mounted pumps by qualified millwright prior to start-up.

  - FIELD QUALITY CONTROL

    - Section 01 45 16.13 - Contractor’s Quality Control Program

    - Perform flow test on entire system in accordance with NFPA 20.

    - Require test to be witnessed by [Fire Marshall] [authority having jurisdiction,] [Owner's insurance underwriter] [Architect/Engineer].

  - DEMONSTRATION AND TRAINING

    - Demonstrate automatic operation of system including verification of pressure switch set points.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2

01/29/2015 Revised Sole Source