READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Air Handling Unit” Work is shown in the Contract Documents. Section includes all accessories.

  - GOVERNING CODES, STANDARDS AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - ARI (Air Conditioning and Refrigeration Institute)

        - ARI 410 - Standard for Forced-Circulation Air-Cooling and Air-Heating Coils.

        - ARI 430 - Standard for Central-Station Air-Handling Units.

        - ARI Guideline D - Application and Installation of Central Station Air-Handling Units.

        - ARI 610 - Central System Humidifiers.

      - AMCA (Air Movement and Control Association)

        - AMCA 99 - Standards Handbook.

        - AMCA 210 - Laboratory Methods of Testing Fans for Rating.

        - AMCA 300 - Reverberant Room Method for Sound Testing of Fans.

        - AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data.

        - AMCA 500 - Test Methods for Louvers, Dampers and Shutters.

      - ABMA (American Bearing Manufacturers Association)

        - ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings.

        - ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings.

      - AGA (American Gas Association)

      - ASHRAE (American Society of Heating, Refrigerating and Air Conditioning Engineers)

        - ASHRAE 51 - Lab Methods of Testing Fans for Rating.

      - FM (Factory Mutual Standards)

      - NEMA (National Electrical Manufacturers Association)

        - NEMA MG1 - Motors and Generators.

      - NFPA (National Fire Protection Association)

        - NFPA 90A - Standard for the Installation of Air Conditioning and Ventilating Systems.

      - SMACNA (Sheet Metal and Air Conditioning Contractors’ National Association)

        - SMACNA - HVAC Duct Construction Standards - Metal and Flexible.

      - UL (Underwriters Laboratories, Inc.)

        - UL 900 - Standard for Air Filter Units.

        - UL - Fire Resistance Directory.

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions.

    - Submittals shall include the following:

      - Shop Drawings: Indicate assembly, unit dimensions, weight loading, required clearances, construction details, field connection details, and electrical characteristics and connection requirements.

      - Indicate DDC control panel, and variable frequency drives locations.

      - Product Data, Submit:

        - Published Literature: Indicate capacities, ratings, gages and finishes of materials, and electrical characteristics and connection requirements.

        - Filters: Data for filter media, filter performance data, filter assembly, and filter frames.

        - Fans: Performance and fan curves with specified operating point clearly plotted, power, RPM.

        - Sound Power Level Data: Fan outlet and casing radiation at rated capacity.

        - Electrical Requirements: Power supply wiring including wiring diagrams for interlock and control wiring, clearly indicating factory-installed and field-installed wiring.

Include the following paragraph for submission of physical samples for selection of finish, color, texture, etc.

      - Samples: Submit two of each type of replacement filter media with frame.

      - Manufacturer's Installation Instructions: Submit.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

  - QUALITY ASSURANCE

    - Provide materials in accordance with the specifications.

Include the following paragraph only when the costs of acquiring the specified standards are justified.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience.

    - Installer: Company specializing in performing Work of this section with minimum three years documented experience approved by manufacturer.

  - DELIVERY, STORAGE, AND HANDLING

    - Accept units and components on site in factory protective containers, with factory shipping skids and lifting lugs. Inspect for damage

    - Protect units from weather and construction traffic by storing in a dry, roofed location.

  - ENVIRONMENTAL REQUIREMENTS

    - Do not operate units until ductwork is clean, filters are in place, bearings lubricated, and fan has been test run under observation.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Supply one set for each unit of fan belts, filters [___]

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - AIR HANDLING UNITS

    - Manufacturers: [Liebert], Haakon, Pace, Miller Picking, Or Approved Equal.

Edit the following descriptive specifications to identify Project requirements. Repeat paragraphs where Project has units configured differently.

    - Configuration: Fan section [fan and coil section] plus accessories, including:

      - Cooling coil section.

      - Heating coil.

      - Humidifier.

      - Filter section.

      - Combination filter/mixing box section.

      - Mixing box section.

      - Face and bypass damper section.

      - Multi-zone damper section.

    - Performance Base: [Sea level] [___] pressure or altitude.

    - Fabrication: Conform to AMCA 99 [and ARI 430.]

To show performance requirements when only one unit is specified, use the following paragraphs. If more than one unit is required, repeat or use a schedule.

    - Air Flow: [___] cfm.

    - External Static Pressure: [___] inch wg.

    - Motor: [___] hp [___] kW.

  - CASING

    - Channel base [and drain pan] of welded steel. Assemble sections with gaskets and bolts.

    - Outside Casing:

      - Aluminum: [0.063] [___] inch thick.

      - Steel: [0.06] [___] inch thick.

      - Galvanized Steel: [0.0516] [0.0635] [___] inch.

      - Finish: Manufacturers standard paint on exterior.

      - Stainless Steel: [0.0625] [___] thick.

    - Inside Casing:

      - Aluminum: [Solid] [Perforated] [0.32] [___] inch thick.

      - Galvanized Steel: [Solid] [Perforated], [0.0276] inch thick.

      - Stainless Steel: [Solid] [Perforated], [0.025] [___] inch thick.

    - Floor Plate:

      - Galvanized Steel: [1.382] [___] inch thick.

      - Stainless Steel: [0.1406] [___] inch thick.

The one-inch thick, 1-1/2 lb/cu ft or 3 lb/cu ft density insulation may be applied with or without weld pins. Thicker insulation requires weld pins.

    - Insulation: Neoprene coated, glass fiber, applied to internal surfaces with adhesive [and weld pins] with exposed edges of insulation coated with adhesive.

      - ‘K’ factor at 75 degrees F: Maximum 0.26 Btuh inch/sq ft/degrees F.

      - Density: [1] [1-1/2] [2] inch thick, [1-1/2] lbs/cu ft.

    - Finish: [Baked enamel] [Zinc chromate, iron oxide, phenolic resin paint] [Asphalt base coating formulated to protect surfaces, to seal seams and joints, and to provide insulation and sound deadening] [Three coat system of epoxy applied over shot-blasted surface, to total thickness of 5-6 mils].

    - Inspection Doors: [10 x 10] [___] inch of galvanized steel for flush mounting, with gasket, latch, and handle assembly [and 1/4 inch thick Plexiglas inspection window]. [Provide welded channel frame to set door out from casing to permit external insulation.]

OR

    - Inspection Doors: [18 x 22] [___] inch of galvanized steel for flush mounting, with gasket, latch, and handle assemblies and 12 x 12 inch inspection window of 1/4 inch thick Plexiglas]. [Provide welded channel frame to set door out from casing to permit external insulation.]

    - Walk-in Access Doors: [18 x 40] [24 x 48] [24 x 60] [30 x 60] [30 x 72] [___] inch Galvanized steel insulated sandwich construction, for flush mounting, with hinges, gasket, latch, and handle assemblies [, and 12 x 12 inch inspection window of 1/4 inch thick Plexiglas]. [Provide welded channel frame to set door out from casing to permit external insulation.]

    - Lights: Provide in accessible sections suitable for damp locations with wire guards, factory wired to [weatherproof] switch [and pilot light] [and duplex outlet] mounted on casing exterior. In humidifier sections, provide lights suitable for wet locations.

    - Drain Pans: [Single] [Double] thickness galvanized steel [with insulation between layers] with welded corners. Cross break and pitch to drain connection. Provide drain pans under [fan section] [heating coil section] [cooling coil section] [mixing section] [humidifier section] [plenum sections] [with asphalt base coating].

    - Bottom Inlet Units: Provide steel or aluminum walking grate on structural supports.

    - Strength: Provide structure to brace casings for suction pressure of [2.5] [___] inch wg, with maximum deflection of 1 in 200.

Use the following three paragraphs for outdoor, roof mounted units.

    - Weatherproof Casing: Seal fixed joints with flexible weather tight sealer. Seal removable joints with closed-cell foam gasket. Provide cap strips over roof flanges. Provide rain caps and gaskets on access doors.

    - Louvers: [Stationary] [Adjustable], of galvanized steel, [4] [6] inch deep with plenum, [nylon bearings,] 1/2 inch mesh, 0.04 inch galvanized wire bird screen in [aluminum] [galvanized] frame, and bearing AMCA Certified Ratings Seal in accordance with AMCA 500. [Furnish adjustable louvers with hollow vinyl bulb edging on blades and foam side stops to limit leakage to maximum 2 percent at 4 inch wg differential pressure when sized for 200 fpm face velocity.]

    - Roof Mounting Curb: Galvanized steel, [12] [14] [___] inches high, insulated with wood nailing strip, and 1/2 x 2 inches neoprene gasket.

  - FANS

    - Manufacturers: Twin Cities, Howden-Buffalo, New York Blower, Or Approved Equal.

    - Type: [Forward curved,] [Backward inclined,] [Air foil,] [single width, single inlet, centrifugal] [double width, double inlet, centrifugal] [Vane axial] [plug] type fan. [Refer to Section 23 34 00 - Fans.]

    - Performance Ratings: Conform to AMCA 210 [and label with AMCA Certified Rating Seal].

    - Sound Ratings: AMCA 301, tested to AMCA 300 [and label with AMCA Certified Sound Rating Seal].

    - Bearings: Self-aligning, grease lubricated, ball or roller bearings with lubrication fittings extended to exterior of casing with [plastic] [aluminum] [copper] tube and grease fitting rigidly attached to casing. [Fan bearings rated at 200,000 hours average life.]

Select one of the next two paragraphs. The first is for units with internally mounted motors, the second for externally mounted motors.

    - Mounting: Locate fan and motor internally on welded steel base coated with corrosion resistant paint. Factory mount motor on slide rails. Provide access to motor, drive, and bearings through removable casing panels or hinged access doors. [Provide built-in inertia base of welded steel with bottom sheet and reinforcing grid for concrete ballast.] Mount base on vibration isolators.

OR

    - Mounting: Locate motor, drive, and belt guard on integral casing framework on exterior of casing. [Provide ventilated weather cover of galvanized steel completely enclosing motor and drive with tachometer opening.] Mount casing on vibration isolators.

    - Fan Accessories: [Variable inlet vanes] [Discharge dampers] [Damper operator]. [Refer to Section 23 34 00 - Fans.]

    - Flexible Connection: Separate unit from connecting ductwork.

To specify fan performance requirements when only one unit is specified, use one of the following paragraphs. If more than one unit is required, repeat for each unit or use a schedule.

    - Supply Fan Performance:

      - Air Flow: [___] cfm.

      - External Static Pressure: [___] inch wg.

      - Motor: [___] hp [___] kW. [Open drip proof] [TEFC] [NEMA MG1, [___].]

    - Return Fan Performance:

      - Air Flow: [___] cfm.

      - External Static Pressure: [___] inch wg.

      - Motor: [___] hp [___] kW . [Open drip proof] [TEFC] [NEMA MG1, [___].]

  - BEARINGS AND DRIVES

Bearing life means that at the rated hours a percent failure is anticipated; i.e., L-10 life at 50,000 hours means that 10 percent of the bearings may be expected to have failed at 50,000 hours.

    - Bearings: Pillow block type, self-aligning, grease-lubricated [ball bearings, with ABMA 9 [L-10 life at 50,000 hours] [L-50 life at 100,000 hours]] [roller bearings, or ABMA 11, [L-10 life at 120,000 hours] [L-50 life at 400,000 hours]].

    - Shafts: Solid, hot rolled steel, ground and polished, with key-way, and protectively coated with lubricating oil.

    - V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, bored to fit shafts, and keyed. Variable and adjustable pitch sheaves for motors 15 hp and under selected so required rpm is obtained with sheaves set at mid-position; fixed sheave for 20 hp and over, matched belts, and drive rated as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor.

    - Belt Guard: Fabricate to SMACNA Standard; 0.106 inch thick, 3/4 inch diamond mesh wire screen welded to steel angle frame or approved equal, prime coated. Secure to fan or fan supports without short circuiting vibration isolation, with provision for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

  - COILS

    - Casing with access to both sides of coils. Enclose coils with headers and return bends [exposed outside] [fully contained within] casing. Slide coils into casing through removable end panel [with blank off sheets and sealing collars at connection penetrations].

    - Drain Pans: 24 inch downstream of coil] and down spouts for cooling coil banks more than one coil high.

    - Eliminators: Three break of [galvanized steel,] [Type 304 stainless steel,] [PVC,] mounted over drain pan.

    - Air Coils: Certify capacities, pressure drops, and selection procedures in accordance with ARI 410.

    - Fabrication:

      - Tubes: 5/8 inch OD seamless copper expanded into fins, brazed joints.

      - Fins: Aluminum.

      - Casing: Die formed channel frame of galvanized steel.

    - Water Heating Coils:

      - Headers: Cast iron, seamless copper tube, or prime coated steel pipe with brazed joints.

      - Configuration: Drainable, with threaded plugs for drain and vent; serpentine type with return bends on smaller sizes and return headers on larger sizes.

    - Steam Heating Coils:

      - Headers: Cast iron with tubes expanded into header, seamless copper tube with silver brazed joints, or prime coated steel pipe with brazed joints.

      - Configuration: Drainable, with threaded plugs for drain and vent, threaded plugs in return bends and in headers opposite each tube, sloped within frame to condensate connection.

    - Steam Distribution Heating Coils:

      - Headers: Cast iron or prime coated steel pipe with brazed joints.

      - Tubes: [5/8] [3/8] inch OD steam distribution tubes located within [one] [5/8] inch OD condensing tubes.

      - Configuration: Drainable, with threaded plugs for drain and vent; with [same end] [opposite end] [double steam] [double pass] connections.

    - Water Cooling Coils:

      - Headers: Cast iron, seamless copper tube, or prime coated steel pipe with brazed joints.

      - Configuration: Drainable, with threaded plugs for drain and vent; threaded plugs in return bends and in headers opposite each tube.

    - Refrigerant Coils:

      - Headers: Seamless copper tubes with silver brazed joints.

      - Liquid Distributors: Brass or copper venturi distributor with seamless copper distributor tubes.

      - Configuration: Down feed with bottom suction.

    - Electric Coils:

      - Assembly: UL 1096 listed and labeled, with terminal control box and [hinged] cover, splice box, coil, casing, and controls.

      - Coil: [Enclosed copper tube, aluminum finned element] [Exposed helical coil].

      - Casing: Die formed channel frame of galvanized steel.

      - Controls: Automatic reset thermal cutout, built-in [magnetic] [mercury] contactors [, control circuit transformer and fuse] [, manual reset thermal cutout] [, air flow proving device] [, fused disconnect] [, non-fused disconnect] [, load fuses].

To specify coil performance requirements when only one unit is specified, use one of the following paragraphs. If more than one unit is required use a schedule.

    - Hot Water Heating Coil:

      - Rows: [___].

      - Capacity: [___] Btuh.

      - Entering Air Temperature: [___] degrees F.

      - Leaving Air Temperature: [___] degrees F.

      - Water Flow Rate: [___] gpm.

      - Entering Water Temperature: [___] degrees F.

      - Leaving Water Temperature: [___] degrees F.

      - Water Pressure Drop: [___] ft head

    - Steam Heating Coil:

      - Rows: [___].

      - Capacity: [___] Btuh.

      - Entering Air Temperature: [___] degrees F.

      - Leaving Air Temperature: [___] degrees F.

      - Steam Flow Rate: [___] lb/hr.

      - Entering Steam Pressure: [___] psi.

    - Water Cooling Coil:

      - Rows: [___].

      - Capacity: [___] Btuh.

      - Entering Air Temperature:

      - Dry Bulb: [___] degrees F.

      - Wet Bulb: [___] degrees F.

      - Leaving Air Temperature:

      - Dry Bulb: [___] degrees F.

      - Wet Bulb: [___] degrees F.

      - Water Flow Rate: [___] gpm.

      - Entering Water Temperature: [___] degrees F.

      - Leaving Water Temperature: [___] degrees F.

      - Water Pressure Drop: [___] ft.

    - Refrigerant Cooling Coil:

      - Rows: [___].

      - Capacity: [___] Btuh.

      - Entering Air Temperature:

      - Dry Bulb: [___] degrees F.

      - Wet Bulb: [___] degrees F.

      - Leaving Air Temperature:

      - Dry Bulb: [___] degrees F.

      - Wet Bulb: [___] degrees F.

      - Refrigerant Saturated Suction Temperature: [___] degrees F.

    - Electric Coil:

      - Capacity: [___] Btuh.

      - Entering Air Temperature: [___] degrees F.

      - Leaving Air Temperature: [___] degrees F.

      - Power Input: [___] kW.

  - BURNER

    - Gas Burner: [Atmospheric] [Induced draft] [Forced draft] type burner with [321 stainless steel heat exchanger] [A.G.A and F.M approved gas train,] adjustable combustion air supply, pressure regulator, [modulating] gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device, and [automatic 100 percent shut-off pilot] [pilot assembly, gravity venting, electric spark ignition pilot relight system, safety pilot].

    - Gas Burner Safety Controls: Energize ignition, limit time for establishment of flame, prevent opening of gas valve until [pilot] [burner] flame is proven, stop gas flow on ignition failure, energize blower motor, and after air flow proven and slight delay, allow gas valve to open, [24 volt control transformer]

    - High Limit Control: Temperature sensor with fixed stop at maximum permissible setting, de-energize burner on excessive bonnet temperature and energize burner when temperature drops to lower safe value.

    - Supply Fan Control: Temperature sensor sensing bonnet temperatures and independent of burner controls, with provisions for continuous fan operation.

  - HUMIDIFIER

    - Provide materials in accordance with the specifications.

Edit the following descriptive specifications to identify Project requirements.

    - Humidifiers: Capacities and selection in accordance with ARI 610.

    - Steam Grid Humidifier: Stainless steel distribution tube with evenly spaced orifices extended full width of unit, factory mounted [in plenum with drain pan for draw-through units] [in diffuser section of blow-through units].

    - Wet Glass Cell Washer Section:

      - 3 inch deep cells with random packed, glass fiber media in [galvanized] [stainless] steel frames.

      - Access Door: Watertight with brass fittings, [wire glass window,] and locking handles.

      - Spray Tree Assembly: [Brass] [Stainless steel] nozzles and [galvanized] [stainless] steel piping.

      - Eliminator: [Galvanized] [Stainless] steel plates.

      - Tank: Welded [stainless] steel [with interior and exterior surfaces blasted and painted with zinc chromate paint]; copper suction screen, drain, overflow, and suction connections; make-up connection with [brass] float valve, and quick-fill connection; insulate exterior with duct insulation and mount on 2 inch thick rigid insulation board.

    - Evaporative Humidifier Section:

      - Access Door: Watertight [cast iron] with brass fittings, wire glass window, and locking handles.

      - Spray Tree Assembly: Brass nozzles and galvanized piping, [galvanized eliminator plates with flooding nozzles and header, and galvanized anti-splash baffles] [cross-fluted cellulose media].

      - Tank: Welded steel tank with interior and exterior surfaces blasted and painted with zinc chromate paint; copper suction screen, drain, overflow, and suction connections; make-up connection with [brass] float valve, and quick-fill connection.

      - Insulation: Duct insulation on exterior and mount on 2 inches thick rigid insulation board.

  - FILTERS

    - Filter Box: Section with filter guides, access doors from both sides, for [side] [face] loading with gaskets and blank-off plates.

    - Filter Media: UL 900 listed, Class I [Class II], approved by [local] [___] authorities.

    - ASHRAE 30% - 2" pleated, 85%/90% 10pocket 22" bags, Charcoal Gas Phase by Extraction Systems Inc.

    - [Flat] [Angle] [High Capacity]: 2 inches] [44 inches] deep [washable permanent panel filters.] [disposable panel filters.] [disposable, extended area panel filters.]

    - Renewable Media: [Horizontal] [Vertical] filters with [manual] [automatic] control [and auxiliary frame for extended surface [retained media filters] [non-supported media filters]]. Motor: [___] hp [___] kW.

    - Extended Surface: Filter box with holding frames and blank-off sheets, extended surface [retained] [non-supported] [high efficiency] media filters with [30] [50] [80] [90] [95] percent dust spot efficiency.

    - Filter Gages: [3-1/2 inch diameter diaphragm actuated dial in metal case,] [2 inch diameter diaphragm actuated dial in metal case,] [One piece molded plastic inclined manometer,] with static pressure tips.

    - Filters: Minimum Efficiency Reporting Value (MERV) shall be in accordance with ASHRAE Standard 52.2.  Filters with MERV 1 to MERV 4 shall also be tested in accordance with ASHRAE Standard 52.1.

    - Filter Media:  UL 900 listed, Class I.

    - Medium Efficiency Pleated Pre-Filters:  All medium efficiency pre-filters shall be ‘pleated’ type and shall contain 100% synthetic media with an ASHRAE 52.2 rating of MERV 8 or greater and an ASHRAE 52.1 average dust spot efficiency of 25-30%.  Filter media shall be hydrophobic.  Pleated pre-filter shall be a ‘high capacity’ model with 18.6 square feet of media per 24x24x2 filter, with an initial resistance of .25”DP at 500 fpm.  The media pack shall be enclosed in a heavy duty, moisture resistant, die cut frame with face grids up and downstream.  Die cut framing shall have a consistent internal coating of adhesive for complete bonding to media pack, providing integrity to the media pack and eliminating air bypass.

    - High Efficiency Bag Type Final Filters:  All high efficiency final filters shall contain 100% synthetic media with an ASHRAE 52.2 rating of MERV 13.  52.1 initial dust spot efficiency of 80% or greater.  Filters shall be a ‘bag type’ design, 24x24x22 10 pocket, with 77 square feet net media area.  Initial resistance at 500 fpm of .25”DP or less.  Media shall be hydrophobic.  Media pockets shall be ‘ultrasonically welded’ to prevent blowout and eliminate the leakage and bypass of ‘stitched’ media construction.

    - Gas Phase Filters:  Filter manufacturers meeting POS approved qualifications and gas phase filter test protocol.

      - FGI Part No. 2710

      - Flanders Vapor Clean Part No. VC-1501-16-01-2424-GD

      - Airguard Vari Klean-Formaldehyde Part No. 15505UKP-05-F

      - Or Approved Equal

    - Initial pressure drop shall be less than 0.45 inches static pressure at 500 feet per minute face velocity. Filter shall be 24"X24"X12" deep and fitted with a frame that is compatible (without rework) with the SeaTac International Airport filter rack (based on ESI Vapor Sorb 1501).

    - Filter Differential Pressure Gage/ Switch: Differential pressure gage/switch with shutoff cocks on each side of differential pressure gage/switch. Provide a differential pressure gage/switch across each filter assembly.

    - 30% Pre Filters, 22” 10 pocket Bag and “POS Approved Gas Phase Filters shall be installed in new air handlers as specified herein before initial startup and at all times during construction, balancing Commissioning and operation.

  - DAMPERS

    - Mixing Boxes: Section with factory mounted outside and return air dampers of galvanized steel [with vinyl bulb edging] [and edge seals] in galvanized frame, with galvanized steel axles in self-lubricating [nylon] [brass] bearings, in [parallel] [opposed] blade arrangement [with damper blades positioned across short air opening dimension.] [Provide removable, full width support for freeze-protection thermostat, with removable end panel to permit support removal.]

    - Damper Leakage: Maximum 2 percent at 4 inch wg differential pressure when sized for 2000 fpm face velocity.

    - Face and Bypass Dampers: Factory mount in casing with access doors, of galvanized steel blades, [with vinyl bulb edging] [and edge seals], galvanized steel frame, and axles in self-lubricating nylon bearings. Arrange to match coil face with [bottom] [top] bypass, blank-off and division sheets, [internal] [external] linkage, access doors, and [adjustable] resistance plate.

    - Multi-Zone Dampers: Factory mount in casing with service door, of galvanized steel blades [with vinyl bulb edging] [and edge seals] and frame with 1/2 inch diameter stainless steel shaft in oil impregnated bronze bearings, with end stops in frame. Arrange for [parallel] [opposed] blade operation, with [adjustable] resistance plates, hand quadrants, and sheet metal clips for duct connections.

  - ELECTRICAL CHARACTERISTICS AND COMPONENTS

Select one or more of the following subparagraphs appropriate to the equipment requirements.

    - Requirements for electrical characteristics:

      - [___] hp ([___ W).] [___ rated load amperes.]

      - [___] volts, [single] [three] phase, 60 Hz.

      - [___] amperes maximum [fuse size] [circuit breaker size] [overcurrent protection].

      - [___] minimum circuit ampacity.

      - [___] percent minimum power factor at rated load.

    - Division 26 Electrical: Requirements for motors.

    - Disconnect Switch: Factory mount [in control panel] [on equipment].

- EXECUTION

  - INSTALLATION

    - Install in accordance with ARI 430.

OR

    - Install flexible connections between unit and inlet and discharge ductwork. Ensure metal bands of connectors are parallel with minimum 1 inch flex between ductwork and fan while running.

    - Install assembled units with vibration isolators. Install isolated fans with resilient mountings and flexible electrical leads. Install restraining snubbers as [indicated] [required]. Adjust snubbers to prevent tension in flexible connectors when fan is operating.

    - Install floor mounted units on concrete housekeeping pads at least 3-1/2 inches high and 6 inches wider than unit.

    - Provide [fixed] sheaves required for final air balance.

    - Make connections to coils with unions or flanges.

    - Hydronic Coils:

      - Hydronic Coils: Connect water supply to leaving airside of coil (counterflow arrangement).

      - Provide shut-off valve on supply line and lockshield balancing valve [with memory stop] on return line.

      - Locate water supply at bottom of supply header and return water connection at top.

      - Provide [manual] [float operated automatic] air vents at high points complete with stop valve.

      - Ensure water coils are drainable and provide drain connection at low points.

    - Steam Coils:

      - Install vacuum breaker in steam line at or in header.

      - Install steam traps with outlet minimum 12 inches below coil return connection.

    - Refrigerant Coils: Provide sight glass in liquid line within 12 inches of coil.

    - Insulate coil headers located outside airflow as specified for piping. Refer to Section 20 07 00 - Mechanical Insulation.

    - Connect humidifiers to water supply. Provide gate valve on water supply line. Provide 3/4-inch hose bib accessible from interior. Pipe drain and overflow to nearest floor drain.

    - Bolt humidifier pumps directly to tank fitting. Provide globe valve and solenoid valve in 1/2 inch bleed line from drain. Provide low water cut-off in drain pan to stop spray pump.

  - FIELD QUALITY CONTROL

    - Section [01 45 16.13 – Contractor’s Quality Control Program.]

    - Section 23 05 93 - Testing, Adjusting, and Balancing.

  - PROTECTION OF INSTALLED CONSTRUCTION

    - Do not permit unit operation without air filters.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions