READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Heating Boilers and Accessories” Work is shown in the Contract Documents. Section includes boilers, controls and boiler trim, steam and condensate connections, hot water connections, fuel burning system and connections, collector, draft hood, draft fan, chimney connections and circulator, expansion tank and tankless water heater options.

  - GOVERNING CODES, STANDARDS AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - AGA (American Gas Association)

        - AGA - Directory of Certified Appliances and Accessories.

      - ANSI (American National Standards Institute)

        - ANSI Z21.13 - Gas-Fired Low-Pressure Steam and Hot Water Boilers.

      - ASME BPVC (American Society of Mechanical Engineers, Boiler and Pressure Vessel Code)

        - ASME BPVC SEC I - Boiler and Pressure Vessels Code - Rules for Construction of Power Boilers.

        - ASME BPVC SEC IV - Boiler and Pressure Vessels Code - Rules for Construction of Heating Boilers.

        - ASME SEC VIII DIV 1 - Boilers and Pressure Vessels Code - Rules for Construction of Pressure Vessels.

      - HI (Hydraulic Institute)

        - HI - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

      - National Board Of Boiler And Pressure Vessel Inspectors

      - NEMA (National Electrical Manufacturers Association)

        - NEMA - Enclosures for Electrical Equipment (1000 Volts Maximum).

      - NFPA (National Fire Protection Association)

        - NFPA 31 - Installation of Oil Burning Equipment.

        - NFPA 54 (AGA Z223.1) - National Fuel Gas Code.

        - NFPA 58 – Liquefied Petroleum Gas Code.

      - International Mechanical Code (IMC)

      - UL (Underwriters Laboratories, Inc.)

        - UL 726 (Underwriters Laboratories, Inc.) - Oil-Fired Boiler Assemblies.

      - State of Washington Boiler and Unfired Pressure Vessel Law

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions.

    - Submittals shall include the following:

      - Product Data: Submit general layout and dimensions. Include size and location of water, fuel, electric and vent connections, electrical characteristics, weight and mounting loads.

      - Test Reports: Indicate specified performance and efficiency is met or exceeded. Provide combustion test that includes boiler firing rate, over fire draft, gas flow rate, heat input, burner manifold gas pressure, percent carbon monoxide (CO), percent oxygen (O), percent excess air, flue gas temperature at outlet, ambient temperature, net stack temperature, percent stack loss, percent combustion efficiency, and heat output.

      - Manufacturer's Installation Instructions: Submit assembly, support details, connection requirements, and include start-up instructions.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

      - Manufacturers Field Reports: Indicate condition of equipment after start-up including control settings and performance chart of control system.

      - Indicate control valves and DDC control panel locations.

      - Include equipment schedules.

  - QUALITY ASSURANCE

Select the appropriate ASME reference; use SEC IV for 15 psi steam or hot water not exceeding 250 degrees or SEC I where steam or hot water exceeds these limits.

    - Conform to ASME SEC I, SEC IV, and AGA Z21.13 Code, UL 726 for construction of boilers. The boiler shall be registered with the National Board Of Boiler And Pressure Vessel Inspectors

    - Unit Certification: AGA certified.

    - Conform to applicable code for internal wiring of factory wired equipment.

    - Products Requiring Electrical Connection: Listed and classified by Underwriters' Laboratories, Inc., testing firm acceptable to the authority having jurisdiction as suitable for the purpose specified and indicated.

Include the following paragraph only when the costs of acquiring the specified standards are justified.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience and with service facilities within 100 miles of Project.

    - Installer: Company specializing in performing Work of this section must have a minimum of three years documented experience and is approved by the manufacturer.

  - DELIVERY, STORAGE, AND HANDLING

Identify any special delivery, storage or handling requirements.

    - Accept boilers and accessories on site in factory shipping packaging. Inspect for damage.

    - Protect boilers from damage by leaving packing in place until installation.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

  - MAINTENANCE SERVICE

    - Provide service and maintenance of boilers for one year from Date of Substantial Completion.

  - MAINTENANCE MATERIALS

    - Provide wire brush and handle for fire tube boiler cleaning.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided. Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Supply one set of circulator pump seals.

- PRODUCTS

  - FINNED WATER TUBE BOILERS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

Use this article carefully; restrict paragraph statements to describe components used to assemble the product.

    - Hot water natural draft boiler with horizontal grid, finned tube heat exchanger, gas burning system, refractory combustion chamber, controls, and boiler trim [including circulator] [and fill system consisting of diaphragm type expansion tank, fill and check valve, and automatic air vent].

  - FINNED WATER TUBE BOILER FABRICATION

    - Assembly: Finned [copper] [or] [steel] tube heat exchanger assembled within combustion chamber conforming to ASME SEC 4 [and SEC 8D] requirements, and tested for maximum working pressure of 160 psi.

    - Combustion Chamber: Line with interlocking refractory insulating panels of vermiculite, high temperature cements, asbestos fiber and refractory clay for service temperatures to 2100 degrees F.

    - Exchanger: Fabricate of [finned copper tubing with stainless steel baffles and sealed into bronze, steel, or cast iron headers with silicone O-ring gaskets] [or] [finned steel tubing with baffles and welded into steel headers].

    - Jacket: Galvanized steel with factory applied baked enamel, insulated with foil faced fiberglass insulation.

  - FINNED WATER TUBE BOILER FUEL BURNING SYSTEM

    - [Induced Draft] [Atmospheric] Gas Burner: Stainless steel burners for [on-off] [hi-low] [modulating] firing and [natural gas] [propane] with adjustable combustion air supply, gas pressure regulator, diaphragm gas valves, manual shut-off, [intermittent spark or glow coil ignition] [standing pilot], thermistor flame sensing device, and automatic 100% safety gas shut-off.

    - Safety Controls: Energize ignition, limit time for establishment of flame, prevent opening of gas valve until pilot flame is proven, stop gas flow on ignition failure, [energize blower motor, and after air flow proven] [and] allow gas valve to open.

    - Flue Gas Collector and Draft Hood: [Integral with boiler casing.] [External draft diverter [with automatic motorized vent damper].] [Integral with boiler casing with built-in [two-speed] induced draft fan, with draft gage and draft providing switches.]

  - FINNED WATER TUBE BOILER TRIM

Select applicable relief valve. Crosscheck the relief valve setting to exceed system pressure relief valve located on expansion tank.

    - ASME rated pressure relief valve set at [45] [60] [___] psi.

    - Low water cut-off or inlet flow switch to automatically prevent burner operation when water falls below safe level or on low flow through boiler.

    - Temperature gage to indicate outlet water temperature

    - Pressure gage with a scale graduated from 1-1/2 to 3 times the safety relief valve set pressure.

  - FINNED WATER TUBE BOILER CONTROLS

    - Operating Controls: Pre-wired, factory assembled electric control including pilot safety and thermocouple transformer, 24-volt gas valve, manual main and pilot valves, and junction box.

Include the following option for boiler manufacturer to supply indoor-outdoor reset controller.

    - Operating temperature controller [with outdoor reset] to control burner operation to maintain supply water temperature.

OR

    - Electronic operating temperature controller:

      - NEMA 250 Type 1 enclosure with full cover for wall mounting.

      - Ambient temperature range of -30 to 150 degrees F.

      - Adjustable reset ratio of outside air temperature change to discharge control point change 1:2 to 100:1.

      - Integral set point adjustment 80 to 230 degrees F.

      - Electronic primary and outdoor sensors.

      - Suitable for on-off switching of pilot duty single-throw double-pole relays.

    - High limit temperature controller with automatic reset for burner to prevent boiler water temperature from exceeding safe system temperature.

  - FINNED WATER TUBE BOILER PERFORMANCE

Use this article carefully; restrict Paragraph statements to identify product performance or product function criteria only.

    - Performance rating in accordance with HI - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

Insert performance requirements essential to Project. Use the following for one or identical units; when specifying units of different size use a schedule.

    - Rating:

      - Input at [sea level] [___] feet altitude: [___] Btu/hr.

      - Output at [sea level] [___] feet altitude: [___] Btu/hr.

  - CAST IRON BOILERS

    - Provide materials in accordance Port of Seattle standards.

Use this paragraph carefully; restrict statements to describe components used to assemble the product.

    - [Hot Water] [Steam] Boilers: [forced] [induced] [natural] draft with insulated jacket, sectional cast iron heat exchanger, [gas] [fuel oil] [gas and fuel oil] burning system, refractory and, controls. [Tankless water heater] and boiler trim [including circulator] [and fill system consisting of diaphragm type expansion tank, fill and check valve and automatic air vent].

Use the following paragraph for forced draft firing boilers.

    - Provide water wall design consisting of water backed combustion area with water circulating around firebox. Refractory chamber or separate base not required.

  - CAST IRON BOILER FABRICATION

    - Assembly: Cast iron sections with [30] [40] [50] [80] [100 psig water] [15 psig steam] ASME Boilers and Pressure Vessels Code rating, assembled with push nipples or gaskets and draw rods.

Use the option in the following paragraph for forced draft firing boilers.

    - Provide Access for flue passages for cleaning [and flame observation ports].

The following paragraph applies to natural draft fired boilers.

    - Structural Base: Aluminized steel lined with high temperature mineral fiber insulating panels.

    - Jacket: Glass fiber insulated steel jacket, finished with factory applied baked enamel.

    - Tankless Water Heater: Finned, copper tube heat exchanger mounted in [top port] [back section below water level].

  - CAST IRON STEAM BOILER TRIM (NOT FOR USE AT SEATAC)

    - ASME rated pressure relief valve, 15 psig.

    - Steam pressure gage, 0 to 30 psig.

    - Water column gage glass set with cocks.

    - Low water cut-off to prevent burner operation when boiler water drops below safe level [and boiler condensate return pump control to maintain water level by controlling pump operation].

    - Operating pressure controller for burner to maintain steam pressure setting.

    - High limit pressure control with manual reset for burner to prevent steam pressure from exceeding system pressure.

  - CAST IRON HOT WATER BOILER TRIM

    - ASME rated pressure relief valve, [30] [40] [50] [80] [100] psig.

    - Combination water pressure and temperature gage. Scale on pressure gage shall be graduated from 11/2 to 3 times the pressure relief valve set pressure

    - Low water cut-off to prevent burner operation when boiler water falls below safe level.

Include the following option for boiler manufacturer to supply indoor-outdoor reset controller.

    - Operating temperature controller [with outdoor reset] to maintain boiler water temperature.

OR

    - Electronic operating temperature controller:

      - NEMA 250 Type 1 enclosure with full cover for wall mounting.

      - Ambient temperature range -30 to 150 degrees F.

      - Adjustable reset ratio of outside air temperature change to discharge control point change 1:2 to 100:1.

      - Integral set point adjustment 80 to 230 degrees F.

      - Electronic primary and outdoor sensors.

      - Suitable for on-off switching of pilot duty with single-throw or double-pole relays.

    - High limit temperature controller with manual reset for burner to prevent boiler water temperature from exceeding safe system temperature.

    - Boiler air vent.

  - CAST IRON BOILER FUEL BURNING SYSTEM

    - Burner Operation: [On-off] [Hi-Low] [modulating] with low fire position for ignition.

    - Oil Burner: High pressure atomizing type for No. 2 fuel oil with combustion air blower, fuel pump, hinged flame inspection port, cadmium sulfide flame sensor, electrodes, ignition transformer, and oil nozzle, fuel filter.

    - Oil Burner Safety Controls: Energize burner motor and electric ignition, limit time for establishment of main flame, monitor flame continuously during burner operation and stop burner on flame failure with manual reset necessary, solenoid oil delay valve opens after burner motor energized and closes when de-energized.

    - Gas Burner: [Atmospheric] [Forced draft] type for [natural gas] [propane] adjustable combustion air supply, pressure regulator, gas valves, manual shut-off, intermittent spark or glow coil ignition, flame sensing device, and automatic 100 percent shut-off.

    - Gas Burner Safety Controls: Energize ignition, limit time for establishment of flame, prevent opening of gas valve until pilot flame is proven, stop gas flow on ignition failure, energize blower motor, and after air flow proven and slight delay, allow gas valve to open.

    - Combination Gas-Oil Burner: Burner for [natural gas] [propane] and No. 2 fuel oil built as unit, equipped with gas pressure regulator and oil-gas selector switch.

    - Collector and Draft Hood: [[Non-metallic] [or] [stainless steel] vent pipe [and air intake].] [Aluminized steel flue collector hood.] [Cast iron smoke hood with integral breeching damper.] [External draft diverter [with automatic motorized vent damper].]

    - Controls: Pre-wired, factory assembled electronic controls in control cabinet with flame scanner or detector, programming control, relays, and switches. Provide pre-purge and post-purge ignition and shut down of burner in event of ignition pilot and main flame failure with manual reset.

  - CAST IRON BOILER PERFORMANCE

Use this paragraph carefully; restrict statements to identify product performance or product function criteria only.

    - Performance rating shall be in accordance with HI - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

Insert performance requirements essential to Project. Use the following for one or identical units; when specifying units of different sizes use a schedule.

    - Rating:

      - Input at sea level: [___] Btu/hr [___] gph.

      - DOE heating capacity: [___] Btu/hr.

      - DOE seasonal efficiency (AFUE) (Annual Fuel Utilization Efficiency): [___] percent.

  - ELECTRIC BOILERS

    - Provide materials in accordance Port of Seattle standards.

    - Description: Electric [hot water] [steam] boiler completely packaged, factory assembled, ready for operation except for connections of piping and electrical connections.

  - ELECTRIC BOILER FABRICATION

    - Assembly: [Welded steel] [or] [Cast iron] shell with heater support nipples or flanges and inspection hand hole. Provide necessary fittings to accept gages, safety and operating controls; threaded or flanged inlet and outlet connections; inlet diffuser; and lifting lugs, conforming to ASME SEC 4 [and SEC 8D] requirements, and tested for maximum working pressure of 160 psig.

    - Heating Elements: Threaded or flanged, [incoloy] [copper] [stainless steel] sheathed, with maximum density of 75 watts per square inch, suitable for operation at 160 psig. Attach each element to tube sheet by mechanical assembly permitting single elements to be replaced without replacing entire tube bundle.

    - Enclose in [galvanized] steel jacket with factory applied baked enamel, insulated with [2 inch] [3 inch] thick fiberglass insulation.

  - ELECTRIC BOILER TRIM

Select a pressure relief-valve rating and insure that this rating exceeds system pressure relief-valve located on expansion tank.

    - ASME rated pressure relief valve set at [45] [60] [___] psi.

    - Assemble with pressure gage, thermometer in brass separable well, automatic air vent and drain valve.

    - Low water cut-off with manual reset [and inlet flow switch] to automatically prevent operation when water falls below safe level [or on low flow through boiler].

Include the following option for boiler manufacturer to supply indoor-outdoor controller.

    - Operating temperature controller [with outdoor reset] with remote bulb in brass separable well to control heating elements to maintain supply water temperature.

    - Electronic operating temperature controller with full cover for wall mounting and ambient temperature range -30 to 150 degrees F Provide adjustable reset ratio of outside air temperature change to discharge control point change varying from 1:2 to 100:1 and integral set point adjustment from 80 to 230 degrees F Provide electronic primary and outdoor sensors, for on-off switching of pilot duty relays.

    - High limit temperature controller with [automatic] [manual] reset to prevent boiler water temperature from exceeding safe system temperature.

  - ELECTRIC BOILER CONTROLS

    - Provide pre-wired, factory assembled electric controls enclosed in NEMA 250, Type 1 cabinet, factory mounted integral with unit.

    - Controls shall include:

      - Non-fused disconnect switch with door interlock.

      - Splitter arrangement and fused magnetic contactors for each element.

      - Fused control circuit transformer with control circuit on/off switch.

      - Proportioning step controller.

      - Remote bulb operating thermostat, complete with brass separable well.

      - Remote bulb high limit thermostat, complete with brass separable well.

      - Pilot lights for each step of control.

      - Terminals for connection of:

        - Peak load control system.

        - Pump motor starter auxiliary contact.

        - Flow switch.

        - Remote mounted three-wire temperature controller.

  - ELECTRIC BOILER PERFORMANCE

Use this paragraph carefully; restrict statements to identify product performance or product function criteria only.

    - Performance rating shall be in accordance with HI - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

Insert performance requirements essential to Project. Use the following for one or identical units; when specifying units of different sizes use a schedule.

    - Rating:

      - Heating capacity: [___] Btu/hr.

      - Number of Steps (Elements): [___].

Include the following two articles when one of the above three boiler types is packaged with a circulator, expansion tank, and related accessories by the manufacturer.

  - CIRCULATOR

    - Type: Horizontal shaft, single stage, direct connected, with resiliently mounted motor for in line mounting, oil lubricated, for 125 psig maximum working pressure.

      - Cast-iron casing.

      - Impeller: Cadmium plated steel, keyed to shaft.

      - Bearings: Oil lubricated bronze sleeves.

      - Shaft: Alloy steel with copper sleeve, integral thrust collar.

      - Seal: Carbon rotating against a stationary ceramic seat, 225 degrees F maximum continuous operating temperature.

      - Drive: Flexible-coupling.

    - Performance:

      - Flow capacity: [___] gal/min.

      - Head: [___] feet.

  - DIAPHRAGM TYPE EXPANSION TANK

    - Construction: Welded steel, tested and stamped in accordance with ASME SEC 8D; rated for working pressure of 125 psig, with flexible diaphragm sealed into tank, and steel legs or saddles.

    - Accessories: Pressure gage and air-charging fitting, tank drain; pre-charge to [12] [___] psig.

    - Size:

      - Diameter: [___] inches.

      - Overall length: [___] inches.

      - Capacity: [___] gallon.

  - FIRE TUBE BOILERS

    - Provide materials in accordance Port of Seattle standards.

    - Description: Factory assembled, factory fire tested, self contained, readily transported unit ready for automatic operation except for connection of [water,] [steam,] fuel, electrical, and vent services.

    - Unit: Mount on integral structural steel frame base and include integral forced draft burner, burner controls, boiler trim, refractory, insulation and jacket.

  - FIRE TUBE BOILER SHELL

Select applicable working pressure and fluid.

    - Construct to applicable ASME Boiler and Pressure Vessels Code for allowable working pressure of [[30] [60] [125] [___] psi water.] [[15] [150] [200] [___] psi steam.]

    - Provide two lifting eyes on top of boiler.

    - Hinged front and rear doors, gas tight, insulated, and secured with heavy-duty cap screws and replaceable brass nuts.

    - Front and rear tube sheets and flue fully accessible for inspection and cleaning when doors are open.

    - Provide observation ports at each end of boiler.

    - Provide hand holes and arm holes for boiler inspection and cleaning.

    - Insulate casing with readily removable, 2-inch thick glass fiber blanket insulation covered by sectional preformed sheet metal jacket. Boiler casing temperature not to exceed ambient room temperature by 18 degrees F maximum with surface air velocity of 1 foot per second.

    - Factory-paint boiler, base, and other components with hard finish silicone enamel.

    - Water entering hot water boiler thoroughly mixed with hot boiler water through jet induced circulation.

    - Provide bi-metal type thermometer, 3-1/2 inch diameter with black letters on white background.

  - FIRE TUBE STEAM BOILER TRIM

    - ASME rated pressure relief valve, [15] [150] [200] [___] psig.

    - Steam pressure gage, graduated from 11/2 to 3 times the safety valve set pressure

    - Water column gage glass set with cocks, low water cut-off [and feedwater pump control].

    - Low water cut-off to prevent burner operation when boiler water drops below safe level [and boiler feedwater pump control to maintain water level by controlling pump operation].

    - Operating pressure controller for burner to maintain steam pressure setting.

    - High limit pressure control with manual reset for burner to prevent steam pressure from exceeding system pressure.

  - FIRE TUBE HOT WATER BOILER TRIM

    - ASME rated pressure relief valve, [30] [40] [50] [80] [100] psig.

    - Water temperature gage.

    - Water pressure gage.

    - Low water cut-off to prevent burner operation when boiler water falls below safe level.

    - Operating temperature controller to control burner to maintain water temperature set point.

    - High limit temperature controller with manual reset for burner to prevent boiler water temperature from exceeding safe system temperature.

    - Boiler air vent. [Manual] [automatic].

  - FIRE TUBE BOILER FUEL BURNING SYSTEM

Edit for applicable burner operation and fuel.

    - General: Forced draft automatic burner integral with front head of boiler designed to burn [natural gas] [and] [No. 2 oil] [No. 5 oil] [No. 6 oil] [No. 4 oil], modulating with low fire ignition position and automatically maintains fuel-air ratio.

      - Blower: Statically and dynamically balanced to supply combustion air; direct connected to motor.

      - Damper Motor: Single motor controlling combustion air damper and fuel valves.

    - Oil Burner: Low pressure atomizing forced draft type with electric ignition [and gas pilot].

      - Oil Pump: Capacity approximately twice the maximum burning rate. Belt driven by blower motor.

      - Oil Burner Piping: Include supply and return tubing to terminal block, oil pressure gage, shut-off cock, and solenoid shut-off valves.

      - Drip Pan: Provide 24 x 24 x 2 inch deep, 16 gage galvanized steel soldered pan on floor under each oil burner.

    - Gas Burner: Forced draft, high-radiant multi-port power burner with electric ignition.

      - Natural Gas Burner Piping: Include on unit complete gas train including high and low gas pressure switches, plug valve, and gas pressure regulator.

    - Combination Gas-Oil Burner: Burner for gas and light oil built as single unit, without need of interchanging. Gas burner and oil burner complete with gas pressure regulator.

  - FIRE TUBE BOILER CONTROL PANEL

    - Mount panel on boiler. Hinged metal cabinet with key lock shall contain programming relay, blower motor starter.

    - Program relay to control ignition, starting and stopping of burner and provide both pre-combustion purge and post combustion purge. Burner to shut down in event of ignition, pilot, or main flame failure. Interlock to shut down burner upon combustion air pressure drop.

    - Manual/automatic selector switch and damper motor positioning switch to permit automatic firing in accordance with load demand, or manual control of firing rate at any desired point between low fire and maximum rating.

    - Electronic detector to prevent primary fuel valves from opening until pilot flame is established.

    - Panel shall include indicating lights to show low water level, flame failure, fuel valve open and load demand. Mount indicating lights and switches in hinged drop-panel for wiring access.

Include for dual/fuel burner.

    - Provide oil/gas fuel selector switch.

  - FIRE TUBE BOILER PERFORMANCE

Use this article carefully; restrict paragraph statements to identify product performance or product function criteria only.

    - Minimum Efficiency: Minimum [76] [80] [___] percent from 30 to 100 percent of full load firing rate, [certified] [verified] by [factory] [and] [site] tests.

    - Capacity:

      - Fluid: [Steam] [Hot water].

      - Input [at sea level]: [___] Btu/hr.

      - Output [at sea level]: [___] Btu/hr.

  - STEEL WATER TUBE BOILERS

    - Provide materials in accordance Port of Seattle standards.

    - Factory assembled, factory fire-tested, self-contained, readily transported unit ready for automatic operation except for connection of [water,] [steam,] fuel, electrical, and vent services.

    - Unit: Steel membrane wall water tube boiler on integral structural steel frame base with integral forced draft burner, burner controls, boiler trim, [tankless water heater,] refractory, insulation, and jacket.

  - STEEL WATER TUBE BOILER SHELL

Select applicable working pressure and medium.

    - Construct to applicable ASME Boiler and Pressure Vessels Code for allowable working pressure of [[30] [60] [125] [140] psi water.] [[15] [150] psi steam.]

    - Provide two lifting eyes on top of boiler.

    - Provide taps, observation ports, removable panels and access doors for entry, cleaning, and inspection.

    - Insulate casing with readily removable glass fiber blanket insulation covered by sectional performed sheet metal jacket.

    - Factory-paint boiler, base, and other components with hard finish silicone enamel.

  - STEEL WATER TUBE STEAM BOILER TRIM

    - Water Column: With cocks, gage glass set and blowdown valves for gage glass and column.

      - Low water cut-off: Integral with water column [with manual reset] to automatically prevent burner operation whenever boiler water falls below safe level.

      - Feedwater pump control: Integral with water column to automatically maintain water level by controlling pump operation.

    - Auxiliary Low Water Cut-off: With drain valve to automatically prevent burner operation whenever boiler water falls below safe level and on failure of primary low water cut-off.

    - Steam Pressure Controls:

      - Auto reset type shall control burner on and off to maintain steam pressure setting.

      - Auto reset type shall control burner firing rate to maintain steam pressure setting.

      - Manual reset type shall control burner to prevent steam pressure from exceeding safe system pressure.

    - ASME rated pressure relief valves.

    - Steam pressure gage with cock and test connection.

  - STEEL WATER TUBE HOT WATER BOILER TRIM

    - Low Water Cut-off: With drain valve and [manual reset] to automatically prevent burner operation whenever boiler water falls below safe level.

    - Temperature Controls:

      - Auto reset type shall control burner on and off to maintain temperature.

      - Auto reset type shall control burner firing rate to maintain temperature.

      - Manual reset type shall control burner to prevent boiler water temperature from exceeding safe system water temperature.

    - Pressure Control: Fixed setting type shall control burner to ensure minimum operating pressure.

    - Blend Pump: Mounted between supply and return connections ensures minimum continuous circulation through boiler.

    - ASME rated pressure relief valves.

    - Combination pressure and thermometer gage.

  - STEEL WATER TUBE FUEL BURNING SYSTEM

Edit for applicable burner operation and fuel.

    - General: Forced draft automatic burner integral with front head of boiler designed to burn [No. 2 oil] [and] [natural gas] and maintain fuel-air ratios automatically.

      - Blower: Statically and dynamically balanced to supply combustion air; direct connected to motor.

      - Damper Motor: Single motor controlling combustion air damper and fuel valves.

    - Oil Burner: Pressure atomizing forced draft type with electric ignition, hi-low firing with low fire ignition position.

      - Oil Pump: Capacity approximately twice the maximum burning rate. Belt driven by blower motor.

      - Oil Burner Piping: Include supply and return tubing to terminal block, oil pressure gage, shut-off cock, and solenoid shut-off valves.

      - Drip Pan: Provide 24 x 24 x 2 inch deep, 16 gage galvanized steel soldered pan on floor under each oil burner.

    - Gas Burner: Forced draft, high-radiant multi-port power burner with electric ignition modulating with low fire ignition position.

      - Natural Gas Burner Piping: Include on unit complete gas train including high and low gas pressure switches, plug valve, and gas pressure regulator.

    - Combination Gas-Oil Burner: Burner for gas and light oil built as single unit, without need of interchanging.

  - STEEL WATER TUBE BOILER CONTROL PANEL

    - Mount NEMA 250, Type 1 hinged metal panel on boiler, containing electronic combustion control, blower motor starter, [low fire hold timer,] automatic-manual firing selection switch, [oil-gas selector switch,] and control switches.

    - Electronic combustion control to control ignition, starting and stopping of burner, and provide both pre-combustion purge and post combustion purge. Burner to shut down in event of ignition, pilot, or main flame failure. Interlock to shut down burner upon combustion air pressure drop.

    - Electronic detector to prevent primary fuel valves from opening until pilot flame is established.

  - STEEL WATER TUBE BOILER PERFORMANCE

Use this paragraph carefully; restrict statements to identify product performance or product function criteria only.

    - Performance rating shall be in accordance with HI - Testing and Rating Standard for Cast Iron and Steel Heating Boilers.

    - Minimum Efficiency: Minimum [76] [80] [___] percent from 30 to 100 percent of full load firing rate, [certified] [verified] by [factory] [and] [site] tests.

Insert performance requirements essential to Project. Use the following for one or identical units; when specifying units of different sizes use a schedule.

    - Capacity:

      - Fluid: [Steam] [Hot water].

      - Input [at sea level]: [___] Btu/hr.

      - Output [at sea level]: [___] Btu/hr.

  - ELECTRICAL CHARACTERISTICS AND COMPONENTS

Select one or more of the following subparagraphs appropriate to the equipment requirements.

    - Refer to Section 26 05 19 - 600 Volt or Less Wire and Cable and Section 26 27 26 - Wiring Devices.

      - [___] hp ([___] W).] [___ rated load amperes.]

      - [___] volts, [single] [three] phase, 60 Hz.

      - [___] amperes maximum [fuse size] [circuit breaker size] [overcurrent protection].

      - [___] minimum circuit ampacity.

      - [___] percent minimum power factor at rated load.

    - Disconnect Switch: Factory-mount [in control panel] [on equipment].

  - SOURCE QUALITY CONTROL (AND TESTS)

Use one or both of the following paragraphs to require owner’s inspection or witnessing of tests at factory.

    - Make completed steel water tube and fire tube boilers available for inspection at manufacturer’s factory prior to packaging for shipment. Notify Owner at least seven days before inspection is allowed.

    - Allow witnessing of factory inspections and tests at manufacturers test facility. Notify Owner at least seven days before inspections and tests are scheduled.

- EXECUTION

  - INSTALLATION

    - Install in accordance with [NFPA 54.] [NFPA 31.] [NFPA 58.]

OR

    - Install Work in accordance with [State of Washington Boiler and Unfired Pressure Vessel Law] [City of Seattle Mechanical Code].

    - ASME code stamp required on all pressure vessels and relief valves. Certificate required from the State Boiler Inspector showing approval of the equipment and its installation, (include in Maintenance Manual).

    - Install equipment in approximate locations indicated on drawings and grout level.

    - [Maintain clearances in accordance with the Seattle Mechanical Code].

    - Obtain and pay for all installation and operating permits.

    - All regulators, valves and other controls required for complete automatic installations must be provided.

    - Install boiler on concrete housekeeping base, minimum 31/2 inches high and 6 inches larger on each side than boiler base. Refer to Section 03 30 00 - Cast-in-Place Concrete.

    - Provide connection of [natural gas] [propane] [fuel oil] service in accordance with [NFPA 54 (AGA Z223.1).] [NFPA 58.] [NFPA 31.]

    - Provide piping connections and accessories as indicated; refer to Section 20 21 16 - Piping Specialties, Section 22 11 16 - Domestic Water Piping, Section 23 20 00 - Heating and Cooling Piping.

    - Pipe relief valves and drain valves to nearest floor drain.

    - Install circulator and diaphragm expansion tank on boiler.

      - Provide for connection to electrical service. Refer to Section 26 05 19 - 600 Volt or Less Wire and Cable and Section 26 27 26 - Wiring Devices.

    - Mount thermometer in boiler breeching within 12 inches of flue nozzle for fire tube boilers. Refer to Section 23 51 00 - Breeching, Chimneys, and Stacks.

  - DEMONSTRATION AND TRAINING

    - Demonstrate operation and maintenance procedures.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions