READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Breeching, Chimneys, and Stacks” Work is shown in the Contract Documents. Section includes fabricated breeching, manufactured chimneys for gas fired equipment, vent dampers, refractory lined chimneys, manufactured double wall chimneys for fuel fired equipment, induced draft fans, single wall metal free-standing stacks.

    - Definitions

      - Breeching: Vent Connector.

      - Chimney: Primarily vertical shaft enclosing at least one vent for conducting flue gases outdoors.

      - Smoke Pipe: Round, single wall vent connector.

      - Vent: That portion of a venting system designed to convey flue gases directly outdoors from a vent connector or from an appliance when a vent connector is not used.

      - Vent Connector: That part of a venting system that conducts the flue gases from the flue collar of an appliance to a chimney or vent, and may include a draft control device.

  - GOVERNING CODES, STANDARDS AND REFERENCES

List reference standards that are included within the text of this section. Edit the following as required for Project conditions.

    - The publications listed below form a part of this specification to the extent referenced. The publications are referred to within the text by the basic designation only.

      - ANSI (American National Standards Institute)

        - ANSI Z21.66 - Automatic Vent Damper Devices for Use with Gas-Fired Appliances.

      - ASTM (American Society for Testing and Materials)

        - ASTM A167 - Stainless and Heat-Resisting Chromium-Nickel Steel Plate, Sheet, and Strip.

        - ASTM A924 - General Requirements for Steel Sheet, Metallic-Coated by the Hot-Dip Process.

        - ASTM A653 - Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

        - ASTM A1011 - Steel, Sheet and Strip, Hot-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability and Ultra-High Strength.

        - ASTM C401 - Classification of Alumina and Alumina Silicate Castable Refractories.

      - NFPA (National Fire Protection Association)

        - NFPA 31 (ANSI Z95.1) - Standard for the Installation of Oil Burning Equipment.

        - NFPA 54 (ANSI Z223.1) - The National Fuel Gas Code.

        - NFPA 82 - Standard on Incinerators, Waste, and Linen Handling Systems and Equipment.

        - NFPA 211 - Standard for Chimneys, Fireplaces, Vents, and Solid Fuel-Burning Appliances.

      - SMACNA (Sheet Metal and Air Conditioning Contractors’ National Association)

        - SMACNA - HVAC Duct Construction Standards - Metal and Flexible.

        - SMACNA - Guide for Steel Stack Construction.

      - UL (Underwriters Laboratories, Inc.)

        - UL 103 - Standard for Factory Built Chimneys for Residential Type and Building Heating Appliances.

        - UL 127 - Standard for Factory Built Fireplaces.

        - UL 378 - Standard for Draft Equipment.

        - UL 441 - Standard for Gas Vents.

        - UL 641- Standard for Type L Low Temperature Venting Systems.

        - UL 959 (ANSI Z181.1) - Medium Heat Appliance Factory Built Chimneys.

  - SUBMITTALS

Only request submittals needed to verify compliance with Project requirements.

    - Submit materials data in accordance with of Section 01 33 00 - Submittals. Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions.

    - Submittals shall include the following:

      - Shop Drawings: For vents, breachings, chimneys, and stacks. Indicate general construction, dimensions, weights, support and layout of breeching. Submit layout drawings indicating plans, elevations, sections, details, and attachments to equipment and other Work.

        - Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, methods of field assembly, supports and hangers, and location and size of each point of connection.

        - For installed products, indicate compliance with codes and design loads. Provide structural analysis with supporting calculations for supports and seismic restraints signed and sealed by a Professional Engineer licensed in the State of Washington.

      - Product Data: Submit data indicating factory built chimneys, including dimensional details of components and flue caps, dimensions and weights, electrical characteristics and connection requirements

Include the following paragraph for submission of physical samples for selection of finish, color, texture, etc.

      - Samples: one sample [___x___] inch in size illustrating finish of chimney and general appearance including flue cap.

      - Manufacturer's Installation Instructions: Submit assembly, support details, and connection requirements.

      - Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

  - DESIGN REQUIREMENTS

Use this article carefully; restrict statements to identify system design requirements only.

    - Factory built vents and chimneys used for venting natural draft appliances shall comply with NFPA 211 and be UL listed and labeled.

    - Design refractory lined metal stacks for wind loading of 110 mph and seismic loads for Zone [___].

  - QUALITY ASSURANCE

Include the following paragraph only when the costs of acquiring the specified standards are justified.

    - Maintain one copy of each document on site.

  - QUALIFICATIONS

    - Manufacturer: Company specializing in manufacturing products specified in this section with minimum three years documented experience.

    - Installer: Company specializing in performing Work of this section with minimum three years documented experience approved by manufacturer.

    - Design stacks over [___] feet above roof under direct supervision of a Professional Engineer experienced in design of this Work and licensed in the State of Washington.

  - ENVIRONMENTAL REQUIREMENTS

    - Maintain water integrity of roof during and after installation of chimney or vent.

  - FIELD MEASUREMENTS

    - Verify field measurements prior to fabrication.

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - BREECHING

    - Fabricate of ASTM A1011 carbon steel. Fabricate breeching less than 24-inch diameter of ASTM A1011 galvanized sheet steel, lock-forming quality with ASTM A924, G90, G165 zinc coating.

    - Fabricate breeching from following minimum gages. Refer to SMACNA HVAC Duct Construction Standards - Metal and Flexible.

      - Sizes up to 12 inches: 18 gage.

      - Sizes 13 to 24 inches: 16 gage.

      - Sizes 25 to 36 inches: 14 gage.

      - Sizes 37 to 60 inches: 12 gage.

      - Sizes over 60 inches: 10 gage.

    - Provide adjustable self-actuating barometric draft dampers, where indicated, full size of breeching.

    - Provide cleanout doors of same gage as breeching, where indicated.

    - Weld longitudinal seams. Fabricate joints by welding, lapping and bolting, or with companion flanges. For breeching less than 24 inches diameter, provide groove seam (pipe lock or flat lock) with end joints beaded and crimped.

    - Reinforce rectangular breeching with angle frames and round breeching with flanged girth joints or angle frames. Refer to SMACNA HVAC Duct Construction Standards - Metal and Flexible.

      - Sizes up to 30 inches: No reinforcing required.

      - Sizes 31 to 36 inches: 1-1/2 x 1-1/2 x 3/16 inches, at 60 inches centers.

      - Sizes 37 to 60 inches: 2 x 2 x 1/4 inch, at 60 inch centers.

      - Sizes over 60 inches: 3 x 3 x 1/2 inch, at 60 inch centers.

    - Fabricate breeching fittings to match adjoining breeching. Fabricate elbows with centerline radius equal to breeching width or diameter. Limit angular tapers to 20 degrees maximum.

  - LISTED TYPE B DOUBLE WALL GAS VENTS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - American Metal Products; MASCO Corporation.

      - Cleaver-Brooks; Div. of Aqua-Chem Inc.

      - Heat-Fab, Inc.

      - Industrial Chimney Company.

      - Metal-Fab, Inc.

      - Selkirk Inc.; Selkirk Metalbestos and Air Mate.

      - Simpson Dura-Vent Co., Inc.; Subsidiary of Simpson Manufacturing Co.

      - Tru-Flex Metal Hose Corp.

      - Van-Packer Company, Inc.

      - Or Approved Equal.

    - Description: Double-wall metal vents tested according to UL 441 and rated for 480 deg F continuously for Type B, or 550 deg F continuously for Type BW; with neutral or negative flue pressure complying with NFPA 211.

    - Construction: Inner shell and outer jacket separated by at least a 1/4-inch airspace.

    - Inner Shell: [ASTM B 209, Type 1100 aluminum], [ASTM B 209, Type 3003 aluminum], [ASTM B 209, Type 3105 aluminum], [ASTM A 666, Type 430 stainless steel].

    - Outer Jacket: Galvanized or Aluminized steel.

    - Electrically, Mechanically, or Thermally Actuated Vent Dampers: Same size as draft hood collar, constructed of stainless steel or galvanized steel, with corrosion-resistant components, in compliance with ANSI Z21.66.

    - Accessories: Tees, elbows, increasers, draft-hood connectors, terminations, adjustable roof flashings, storm collars, support assemblies, thimbles, firestop spacers, and fasteners; fabricated from similar materials and designs as vent-pipe straight sections; all listed for same assembly.

      - Termination: Stack cap designed to exclude minimum 90 percent of rainfall.

      - Termination: Round chimney top designed to exclude minimum 98 percent of rainfall.

      - Termination: Exit cone with drain section incorporated into riser.

      - Termination: Antibackdraft.

      - Termination: See schedule on drawings. Double-wall metal vents.

  - LISTED, REFRACTORY LINED METAL STACKS

    - Manufacturers: Subject to compliance with Design Requirements, provide products from one of the following:

      - Van-Packer Company, Inc.

      - Warren Environmental, Inc.

      - Or Approved Equal.

    - Fabricate jacket for size 36 inches and smaller of 24 gage galvanized steel with grooved seam joint, or 26 gage aluminized steel with riveted seams. For sizes 39 inches and larger fabricate of 11 gage galvanized steel with welded seam joint.

    - Weld heavy-gage stack sections to other sections. Apply heat resistant paint to each stack section and accessory with primer and finish paint in factory. Touch-up or refinish in field.

    - Provide refractory lining of minimum 2 inch thick, ASTM C401 Class [___] tested to UL 959 and UL listed to withstand 2000 degrees F without fusion. Provide lining with a maximum acid extraction of 0.2 percent, have minimum of 3200 psi cold crush strength, and be positively bonded to steel jacket, jointed with ASTM C105 mortar.

    - Accessories, UL labeled:

      - Anchor Lugs: Acid resistant coated cast iron.

      - Clean Out Section: Welded to base of stack, with gasket, and bolt tightened inspection plate.

      - Branching Sections: Construct with welded joints, lined with refractory, finished with smooth transition and no exposed metal on inside.

      - Spark Screen: Type 304 stainless steel, 16 gage 1/2 x 1/2 inch mesh, with rolled angle and draw band.

      - Drawbands: 8-inch wide, same material as jacket, fastened with nuts and bolts.

      - Roof Penetration: Factory fabricated thimble, flashing and storm collar.

  - DOUBLE WALL METAL STACKS

    - Provide double wall metal stacks, tested to UL 103, UL 127, UL 641 and UL listed, for use with building heating equipment, in compliance with NFPA 211.

    - Fabricate with 1-inch minimum air space between walls. Construct inner jacket of 20 gage ASTM A167 Type 304, Type 316 stainless steel. Construct outer jacket of aluminum coated steel, Type 304, Type 316 stainless steel 24 gage for sizes 10 inches to 24 inches and 20 gage for sizes 28 inches to 48 inches.

    - Accessories, UL labeled:

      - Ventilated Roof Thimble: Consists of roof penetration, vent flashing with spacers and storm collar.

      - Exit Cone: Consists of inner cone, and outer jacket, to increase stack exit velocity 1.5 times.

      - Stack Cap: Consists of conical rainshield with inverted cone for partial rain protection with low flow resistance.

  - SINGLE WALL METAL STACKS

    - Provide single wall metal stacks in accordance with the SMACNA Guide for Steel Stack Construction.

      - Stack size: diameter, wall thickness and height.

      - Stack design wind velocity: [100], [125], [150] miles per hour.

      - Stack: damped, undamped.

      - Stack wall material: hot-rolled steel, galvanized steel.

    - When stack wall thickness is different than the NFPA 211 minimum then the stack wall thickness shall conform to the accepted engineering design provisions of the SMACNA Guide.

    - Provide stack base plate and anchor details as specified in the SMACNA Guide for anchorage to a concrete ground level foundation with a minimum compressive strength of 4.00 psi. Concrete foundation as indicated.

  - INDUCED DRAFT FANS

    - Mechanical Draft Induction Type:

      - Venturi Tube Section: Enameled steel for sizes up to 20 inch and Type 304 stainless steel for sizes 22 inch to 48 inch diameter.

      - Fan: Forward curved venturi type, tested to UL 378, with shaded pole, sleeve bearing, open drip proof, ball bearing motor.

    - Induced Draft Type:

      - Forward curved fan and scroll of mild steel with direct drive shaded pole motor with ball bearings, internal cooling fan, stainless steel shaft, and internal centrifugal switch, tested to UL 378.

      - Capacity: [___] cu ft/min standard air at [___] inch negative static pressure, and [___] inch negative static pressure at tight suction shut-off.

    - Motor: [___] hp.

    - Wiring Terminations: Provide terminal lugs to match branch-circuit conductor quantities, sizes, and materials indicated. Enclose terminal lugs in terminal box.

- EXECUTION

  - INSTALLATION

    - Install in accordance with NFPA 54 (ANSI Z223.1), NFPA 31, SMACNA Guide for Steel Stack Construction.

    - Install breeching with minimum of joints. Align accurately at connections, with internal surfaces smooth.

    - Support breeching from building structure, rigidly with suitable ties, braces, hangers and anchors to hold to shape and prevent buckling. Support vertical breeching, chimneys, and stacks at 12-foot spacing, to adjacent structural surfaces, or at floor penetrations. Refer to SMACNA HVAC Duct Construction Standards - Metal and Flexible for equivalent duct support configuration and size.

    - Install concrete inserts for support of breeching, chimneys, and stacks in coordination with formwork.

    - Pitch breeching with positive slope up from fuel-fired equipment to chimney or stack.

    - Coordinate installation of dampers, and induced draft fans.

    - Insulate breeching in accordance with Section 20 07 00 - Mechanical Insulation.

    - For Type B double wall gas vents, maintain UL listed minimum clearances from combustibles. Assemble pipe and accessories as required for complete installation.

    - Install vent dampers, locating close to draft hood collar, and secured to breeching.

    - Assemble and install stack sections in accordance with NFPA 82, industry practices, and in compliance with UL listing. Join sections with acid-resistant joint cement to ASTM C105. Connect base section to foundation using anchor lugs.

    - Level and plumb chimney and stacks.

    - Clean breeching, chimneys, and stacks during installation, removing dust and debris.

    - At appliances, provide slip joints permitting removal of appliances without removal or dismantling of breeching, breeching insulation, chimneys, or stacks.

    - Provide minimum length, maximum 2 feet of breeching to connect appliance to chimney. Provide Type B chimney continuously from appliances.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions