READ THIS FIRST

Notice to the Design Engineer, please refer to the Port of Seattle, Facilities and Infrastructure standards for reference before editing this specification.

This Project Spec Document may need additional modifications to suit your project. It is recommended that you proofread each section, paying attention to any “Notes” boxes such as this one--you should remove these “Notes” sections as you go. Also, do a search for all bracket characters “ [ ] “ as they are used to show you areas containing options or project specific details (you can use Microsoft Word’s Find feature {Ctrl-F} to jump to an open bracket “ [ “ character quickly). Again, these bracket characters should be removed.

It is important that every paragraph be numbered to allow for easy referencing. If you use the document’s built in styles and formatting your outline should be fine (turn on the formatting toolbar by going to View > Toolbars > Formatting). Most paragraphs will use the style “Numbered Material” and can be promoted (Shift) or demoted (Shift-Tab).

You should not have to manually enter extra spaces, carriage returns or outline characters such as A, B, C, or 1.01, 1.02; the formatting will do this for you. The entire document is 11 pt. Arial. If you paste items in, you may need to reapply the “Numbered Material” format.

- GENERAL

  - SUMMARY OF WORK

    - The extent and location of “Motor Controllers” Work is shown in the Contract Documents. This section includes motor controllers rated 600V and less that are supplied as enclosed units.

  - GOVERNING CODES, STANDARDS AND REFERENCES

    - IEEE C62.41 (Institute of Electrical and Electronics Engineers) - Recommended Practice on Surge Voltages in Low-Voltage AC Power Circuits.

    - UL 489 - Molded Case Circuit Breakers, Molded-Case Switches and Circuit-Breaker Enclosures.

    - NEMA FU 1 (National Electrical Manufacturers Association) – Low Voltage Cartridge Fuses.

    - NEMA ICS 2 (National Electrical Manufacturers Association) - Industrial Control and Systems: Controllers, Contactors, and Overload Relays, Rated Not More Than 2000 Volts AC or 750 Volts DC.

    - NEMA ICS 3 (National Electrical Manufacturers Association) - Industrial Control and Systems: Factory Built Assemblies.

    - NEMA ICS 5 (National Electrical Manufacturers Association) - Industrial Control and Systems: Control Circuit and Pilot Devices.

    - NEMA KS 1 (National Electrical Manufacturers Association) – Heavy Duty Enclosed and Dead-Front Switches (600 Volts Maximum).

    - NETA ATS (International Electrical Testing Association) - Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems.

    - NFPA 70 (National Fire Protection Association) - National Electrical Code.

  - SUBMITTALS

    - Submit materials data in accordance with of Section 01 33 00 - Submittals.  Furnish manufacturers’ technical literature, standard details, product specifications, and installation instructions for all products.

    - Submittals shall include the following:

      - Product Data: For each type of enclosed controller. Include dimensions and manufacturer’s technical data on features, performance, electrical characteristics, ratings, and finishes.

      - Shop Drawings: For each motor controller.

        - Dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment. Show tabulations of installed devices, equipment features, and ratings. Include the following:

          - Enclosure types and details.

          - Factory-installed devices.

          - Nameplate legends.

          - Short-circuit current rating of integrated unit.

          - UL listing for series rating of overcurrent protective devices in combination controllers.

          - Features, characteristics, ratings, and factory settings of individual overcurrent protective devices in combination controllers.

        - Wiring Diagrams: Power, signal, and control wiring. Differentiate between manufacturer-installed and field-installed wiring.

      - Manufacturer Seismic Qualification Certification: Submit certification that enclosed controllers, accessories, and components will withstand seismic forces defined in Section 26 05 48 - Seismic Controls for Electrical and Communication Work. Include the following:

        - Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

          - The term “withstand” means “the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event.”

        - Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

        - Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

      - Field Test Reports: Written reports specified in Part 3.

      - Manufacturer’s field service report.

      - Maintenance Data: For enclosed controllers and components to include in maintenance manuals specified in Division 1 General Requirements. In addition to requirements specified in Section 01 78 23.13 - Operations and Maintenance Data include the following:

        - Parts list.

        - Wiring schematics/diagrams and heater tables.

        - Routine maintenance requirements for enclosed controllers and all installed components.

        - Manufacturer’s written instructions for testing and adjusting overcurrent protective devices.

Select one of the two following paragraphs below to suit type of motor running overload protection specified in Part 2.

      - Load-Current and Overload-Relay Heater List: Compile after motors have been installed and arrange to demonstrate that selection of heaters suits actual motor nameplate full-load currents.

      - Load-Current and List of Settings of Adjustable Overload Relays: Compile after motors have been installed and arrange to demonstrate that dip-switch settings for motor running overload protection suit actual motor to be protected.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Maintain, within 100 miles of Project site, a service center capable of providing training, parts, and emergency maintenance and repairs.

    - Source Limitations: Obtain controllers of a single type through one source from a single manufacturer in service for at least 10 years.

    - Listing and Labeling: Provide components, devices and accessories that are Listed and Labeled as defined in NFPA 70, Article 100 and marked for intended use for the location and environment in which they are installed.

    - Comply with NFPA 70, as adopted and administered by the Authority Having Jurisdiction.

Retain below to allow drawing details based on one manufacturer’s product to establish requirements and still allow competition. Delete if controllers are small and wall mounted and space is not a concern.

    - Product Selection for Restricted Space: Drawings indicate maximum dimensions for enclosed controllers, including clearances between enclosed controllers, and for adjacent surfaces and other items. Comply with indicated maximum dimensions.

  - DELIVERY, STORAGE, AND HANDLING

Revise this Article to refer to other Divisions, such as Division 14 Conveying Equipment for baggage conveyor systems, if control coordination is required.

For large controllers, include both paragraphs below; delete second paragraph if indoor space is likely to be available at Project site.

    - Store enclosed controllers indoors in clean, dry space with uniform temperature to prevent condensation. Protect enclosed controllers from exposure to dirt, fumes, water, corrosive substances, and physical damage.

      - If stored in areas subjected to weather, cover enclosed controllers to protect from weather, dirt, dust, corrosive substances, and physical damage. Remove loose packing and flammable materials from inside controllers; install electric heating of sufficient wattage to prevent condensation.

  - COORDINATION

    - Coordinate layout and installation of enclosed controllers with other construction including conduit, piping, equipment, and adjacent surfaces. Maintain required workspace clearances and required clearances for equipment access doors and panels.

Retain paragraph below if required for base-supported enclosed controllers.

    - Coordinate size and location of concrete bases. Refer to Section 03 30 00 - Cast-in-Place Concrete for concrete, reinforcement, and formwork requirements.

    - Coordinate features of enclosed controllers and accessory devices with pilot devices and control circuits to which they connect.

    - Coordinate features, accessories, and functions of each enclosed controller with ratings and characteristics of supply circuit, motor, required control sequence, and duty cycle of motor and load.

  - EXTRA MATERIALS

    - Spare and extra parts shall be identified for all products, but not provided.  Include spare parts information in Operation and Maintenance Manuals.

Include spare parts information in Operation and Maintenance Manuals.

Spare Fuses: [3] of each type and rating installed.  [1 spare for every 5 installed units, but not less than 1 set of 3 of each kind.]

Indicating Lights: [2] of each type and rating installed.

Furnish 1 spare for every 5 installed units, but not less than 1 set of 3 of each kind

- PRODUCTS

A.	If only one product is acceptable (single or sole source product), obtain an approved Competition Waiver and submit to the CPO Construction, Contract Administrator.  The language shall read as: “Manufacturer Name, Product # XXXXX, No Equal.”  Refer to CPO-6 Competition Waiver Policy for more information.

B.	If a Competition Waiver is not approved or more than one product is acceptable, this section must list a minimum of 2 products plus the language “Or Approved Equal,” along with salient characteristics.  Refer to CPO Construction’s Salient Characteristics Guidelines for more information.

  - MANUFACTURERS

    - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

      - Allen-Bradley

      - Cutler-Hammer

      - General Electric

      - Square D

      - Or Approved Equal.

  - ENCLOSURES

    - NEMA ICS 6, Type to meet environmental conditions at installed location:

      - Indoor Clean, Dry Locations: NEMA 250, Type 1.

      - Indoor Locations Subject to Wet or Dry Contaminants: NEMA 250, Type 12.

      - Outdoor or Damp Locations: NEMA 250, Type [3R] [4].

      - Corrosive Locations: NEMA 250, Type 4X, stainless steel.

      - Hazardous Locations: NEMA 250, Type 7 to meet NFPA hazardous classification.

  - GENERAL

    - Provide reduced-voltage starters for centrifugal horsepower sizes for voltages and sizes as noted below:

      - 5 HP and larger - 208V, 3-phase

      - 5 HP and larger - 480V, 3-phase

    - Positive displacement loads shall have reduced voltage starters

  - STARTING METHODS MAY INCLUDE, BUT ARE NOT LIMITED, TO THE FOLLOWING

    - Manual

    - Magnetic Full Voltage Non-reversing (FVNR)

    - Magnetic Full Voltage reversing (FVR)

    - Magnetic Reduced Voltage Autotransformer (RVAT)

    - Magnetic Reduced Voltage Part Winding

    - Magnetic Reduced Voltage Wye Delta open or closed transition

    - Magnetic two speed one or two winding

    - Solid-state reduced voltage

    - Solid-state reduced voltage with contactor bypass

    - Solid-state soft start

  - FULL-VOLTAGE CONTROLLERS

    - General Requirements for Full-Voltage Controllers: Comply with NEMA ICS 2, general purpose, Class A.

    - Motor-Starting Switches: "Quick-make, quick-break" toggle or push-button action; marked to show whether unit is off or on.

      - Configuration: Nonreversing OR Reversing OR Two speed.

      - Pilot Light:

        - Mounted in front of panel.

        - Red indicates “running”.

        - Green indicates “ready”.

        - Standard pilot lights are 120V, transformer type, push-to-test.

      - Additional Nameplates: FORWARD and REVERSE for reversing switches, HIGH and LOW for two-speed switches.

    - Fractional Horsepower Single phase Manual Controllers: "Quick-make, quick-break" toggle or push-button action; marked to show whether unit is off, on, or tripped.

      - Configuration: Nonreversing OR Two speed.

      - Lockout means required in all applications.

      - Fault duty to meet available fault current.

      - Interchangeable overload heater elements.

      - Overload Relays: Inverse-time-current characteristics; NEMA ICS 2, Class 10 tripping characteristics; heaters matched to nameplate full-load current of actual protected motor; external reset push button; bimetallic type or melting alloy type.

      - Red pilot light to indicate “running.”

      - Additional Nameplates: HIGH and LOW for two-speed controllers.

    - Integral Horsepower Manual Controllers: "Quick-make, quick-break" toggle or push-button action; marked to show whether unit is off, on, or tripped.

      - Configuration: Nonreversing, reversing or two speed, depending on engineering considerations.

      - Overload Relays: Inverse-time-current characteristics; NEMA ICS 2, Class 10 tripping characteristics; heaters and sensors in each phase, matched to nameplate full-load current of actual protected motor and having appropriate adjustment for duty cycle; external reset push button; bimetallic type or melting alloy type.

      - Red and Green pilot light.

      - Additional Nameplates: FORWARD and REVERSE for reversing controllers OR HIGH and LOW for two-speed controllers.

      - One each N.O. and N.C. reversible auxiliary contact.

    - Magnetic Controllers: Full voltage, across the line, electrically held.

      - Configuration: Nonreversing OR reversing, based on engineering considerations.

      - Contactor Coils: Pressure-encapsulated type with coil transient suppressors.

        - Operating Voltage: Depending on contactor NEMA size and line-voltage rating, manufacturer's standard matching control power or line voltage.

      - Power Contacts: Totally enclosed, double-break, silver-cadmium oxide; assembled to allow inspection and replacement without disturbing line or load wiring.

      - Control Circuits: 120-V ac; obtained from integral CPT, with primary and secondary fuses, with CPT of sufficient capacity to operate integral devices and remotely located pilot, indicating, and control devices.

        - CPT Spare Capacity: Size CPT at least one size above minimum VA requirements.

      - Melting Alloy Overload Relays:

        - Inverse-time-current characteristic.

        - Class 10 tripping characteristic.

        - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

      - Bimetallic Overload Relays:

        - Inverse-time-current characteristic.

        - Class 10 tripping characteristic.

        - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

        - Ambient compensated where required by engineering requirements.

        - Automatic resetting.

      - Solid-State Overload Relay:

        - Switch or dial selectable for motor running overload protection. Software selectable is not acceptable.

        - Sensors in each phase.

        - Class 10 tripping characteristic selected to protect motor against voltage and current unbalance and single phasing.

        - Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

        - IP addressable communication module.

      - One each N.C. and N.O. reversible isolated overload alarm contact.

      - External overload reset push button.

    - Combination Magnetic Controller: Factory-assembled combination of magnetic controller, OCPD, and disconnecting means.

      - Sizes 1 through 5 are standard for all applications.

      - Motor controller preferred features include:

        - Current sensor/microprocessor-type overload protection with adjustable parameters including overcurrent, ground fault, phase loss, phase unbalance, undervoltage and overvoltage.

        - Melting alloy or bimetallic strip type overload relays with ambient compensated inverse time-current characteristics are acceptable.

        - Control pushbuttons, industrial oil-tight type.

        - Push-to-test pilot lights.

      - Fusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate indicated fuses.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - Nonfusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, nonfusible switch.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - MCP Disconnecting Means:

        - Use where available fault current is 65,000 Amps symmetrical or less.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable up to 1300% of motor FLA, short-circuit trip coordinated with motor locked-rotor amperes.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

      - MCCB Disconnecting Means:

        - Use where available fault current exceeds 65,000 AIC.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

        - Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

  - REDUCED-VOLTAGE MAGNETIC CONTROLLERS

    - General Requirements for Reduced-Voltage Magnetic Controllers: Comply with NEMA ICS 2, general purpose, Class A; closed-transition; adjustable time delay on transition.

    - Reduced-Voltage Magnetic Controllers: Reduced voltage, electrically held.

      - Configuration:

        - Wye-Delta Controller: Four contactors, with a three-phase starting resistor/reactor bank. Open or closed transition.

        - Part-Winding Controller: Separate START and RUN contactors, field-selectable for 1/2- or 2/3-winding start mode, with either six- or nine-lead motors; with separate overload relays for starting and running sequences.

        - Autotransformer Reduced-Voltage Controller: Medium-duty service, with integral overtemperature protection; taps for starting at 50, 65, and 80 percent of line voltage; two START and one RUN contactors.

      - Contactor Coils: Pressure-encapsulated type with coil transient suppressors.

        - Operating Voltage: Depending on contactor NEMA size and line-voltage rating, manufacturer's standard matching control power or line voltage.

      - Power Contacts: Totally enclosed, double-break, silver-cadmium oxide; assembled to allow inspection and replacement without disturbing line or load wiring.

      - Control Circuits: 120-V ac; obtained from integral CPT, with primary and secondary fuses, with CPT sized at least one size above the minimum VA requirements. Should an external power source be required, provide auxiliary contacts mechanically tied to the combination starter disconnect switch and wire so that control power within the motor starter module will be disconnected when the motor power disconnect is opened. The secondary of the CPT shall have one leg grounded. No switching of coils shall be allowed between the coil and the ground side.

      - Melting Alloy Overload Relays:

        - Inverse-time-current characteristic.

        - Class 10 tripping characteristic.

        - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

      - Bimetallic Overload Relays:

        - Inverse-time-current characteristic.

        - Class 10 tripping characteristic.

        - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

      - Solid-State Overload Relay:

        - Switch or dial selectable for motor running overload protection. Software selectable controls are not allowed.

        - Sensors in each phase.

        - Class 10 tripping characteristic selected to protect motor against voltage and current unbalance and single phasing.

        - Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

        - IP addressable communication module.

      - One each N.C. and N.O. reversible, isolated overload alarm contact.

      - External overload reset push button.

    - Combination Reduced-Voltage Magnetic Controller: Factory-assembled combination of reduced-voltage magnetic controller, OCPD, and disconnecting means.

      - Sizes 1 through 5 are standard for all applications.

      - Motor controller preferred features include:

        - Current sensor/microprocessor-type overload protection with adjustable parameters including overcurrent, ground fault, phase loss, phase unbalance, undervoltage and overvoltage.

        - Melting alloy or bimetallic strip type overload relays with ambient compensated inverse time-current characteristics are acceptable.

      - Fusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate indicated fuses.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - Nonfusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, nonfusible switch.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - MCP Disconnecting Means:

        - Use where available fault current is 65,000 Amps symmetrical or less.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable up to 1300% of motor FLA, short-circuit trip coordinated with motor locked-rotor amperes.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

      - MCCB Disconnecting Means:

        - Use where available fault current exceeds 65,000 Amps symmetrical.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

        - Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

  - REDUCED-VOLTAGE SOLID-STATE CONTROLLERS

    - General Requirements for Reduced-Voltage Solid-State Controllers: Comply with UL 508.

    - Reduced-Voltage Solid-State Controllers: An integrated unit with power semiconductors, heat sink, microprocessor logic board, door-mounted digital display and keypad, bypass contactor, and overload relay; suitable for use with NEMA MG 1, Design B, polyphase, medium induction motors.

      - Configuration: Heavy duty, reversible OR non-reversible, depending on engineering considerations.

      - Starting Mode: Voltage ramping OR Current limit OR Torque control OR Torque control with voltage boost OR; field selectable, depending on application.

      - Stopping Mode: Coast to stop OR Adjustable torque deceleration OR Adjustable braking OR field selectable, depending on application.

      - Shorting (Bypass) Contactor: Operates automatically when full voltage is applied to motor, and bypasses the power semiconductors. Solid-state controller protective features shall remain active when the shorting contactor is in the bypass mode.

      - Shorting and Input Isolation Contactor Coils, if required by project parameters: Pressure-encapsulated type; manufacturer's standard operating voltage, matching control power or line voltage, depending on contactor size and line-voltage rating. Provide coil transient suppressors.

      - Logic Board: Identical for all ampere ratings and voltage classes, with environmental protective coating.

      - Control Circuits: 120-V ac; obtained from integral CPT, with primary and secondary fuses, with CPT of sufficient capacity to operate integral devices and remotely located pilot, indicating, and control devices.

        - CPT Spare Capacity: Size CPT at least one size above minimum VA requirements.

      - Adjustable acceleration-rate control using voltage or current ramp, and adjustable starting torque control with up to 400 percent current limitation for 20 seconds.

      - Keypad, front accessible; for programming the controller parameters, functions, and features; shall be manufacturer's standard and include not less than the following functions:

        - Adjusting motor full-load amperes, as a percentage of the controller's rating.

        - Adjusting current limitation on starting, as a percentage of the motor full-load current rating.

        - Adjusting linear acceleration and deceleration ramps, in seconds.

        - Initial torque, as a percentage of the nominal motor torque.

        - Adjusting torque limit, as a percentage of the nominal motor torque.

        - Adjusting maximum start time, in seconds.

        - Adjusting voltage boost, as a percentage of the nominal supply voltage.

        - Selecting stopping mode, and adjusting parameters.

        - Selecting motor thermal overload protection class between 5 and 30.

        - Activating and de-activating protection modes.

      - Digital display, front accessible; for showing motor, controller, and fault status; shall be manufacturer's standard and include not less than the following:

        - Controller Condition: Ready, starting, running, stopping.

        - Motor Condition: Amperes, voltage, power factor, power, and thermal state.

        - Fault Conditions: Controller thermal fault, motor overload alarm and trip, motor underload, overcurrent, shorted power semiconductors, line or phase loss, phase reversal, and line frequency over or under normal.

      - Controller Diagnostics and Protection:

        - Microprocessor-based thermal protection system for monitoring power semiconductor and motor thermal characteristics, and providing controller overtemperature and motor-overload alarm and trip; settings selectable via the keypad.

        - Protection from line-side reverse phasing; line-side and motor-side phase loss; motor jam, stall, and underload conditions; and line frequency over or under normal.

        - For controllers without integral disconnects, provide input isolation contactor that opens when the controller diagnostics detect a faulted solid-state component or when the motor is stopped.

        - For combination motor starter/disconnect, provide shunt trip that opens the disconnecting means when the controller diagnostics detect a faulted solid-state component.

      - Remote Output Features:

        - All outputs prewired to terminal blocks.

        - Form C status contacts that change state when controller is running.

        - Form C alarm contacts that change state when a fault condition occurs.

      - Optional Features:

        - Analog output for field-selectable assignment of motor operating characteristics; 4 to 20-mA dc.

        - Additional field-assignable Form C contacts, as indicated, for alarm outputs.

        - Surge suppressors in solid-state power circuits providing three-phase protection against damage from supply voltage surges 10 percent or more above nominal line voltage.

        - Melting Alloy Overload Relays:

          - Inverse-time-current characteristic.

          - Class 10 tripping characteristic.

          - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

        - Bimetallic Overload Relays:

          - Inverse-time-current characteristic.

          - Class 10 tripping characteristic.

          - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

          - Ambient compensated.

        - Solid-State Overload Relay:

          - Switch or dial selectable for motor running overload protection. Software selectable controls are not allowed.

          - Sensors in each phase.

          - Class 10 tripping characteristic selected to protect motor against voltage and current unbalance and single phasing.

          - Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

          - IP addressable communication module.

        - One each N.C. and N.O. reversible, isolated overload alarm contact.

        - External overload reset push button.

    - Combination Reduced-Voltage Solid-State Controller: Factory-assembled combination of reduced-voltage solid-state controller, OCPD, and disconnecting means.

      - Fusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate indicated fuses.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - MCP Disconnecting Means:

        - Use where available fault current is 65,000 Amps symmetrical or less.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable up to 1300% of motor FLA, short-circuit trip coordinated with motor locked-rotor amperes.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

      - MCCB Disconnecting Means:

        - Use where available fault current exceeds 65,000 Amps symmetrical.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

        - Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

      - Molded-Case Switch Disconnecting Means:

        - UL 489, UL 489, and NEMA AB 3, with in-line fuse block for Class J or L power fuses (depending on ampere rating), providing an interrupting capacity to comply with available fault currents; MCCB with fixed, high-set instantaneous trip only.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

  - MULTISPEED MAGNETIC CONTROLLERS

    - General Requirements for Multispeed Magnetic Controllers: Comply with NEMA ICS 2, general purpose, Class A.

    - Multispeed Magnetic Controllers: Two speed, full voltage, across the line, electrically held.

      - Configuration: One or two winding, reversing or non-reversing, depending on project requirements.

      - Contactor Coils: Pressure-encapsulated type with coil transient suppressors.

        - Operating Voltage: Depending on contactor NEMA size and line-voltage rating, manufacturer's standard matching control power or line voltage.

      - Power Contacts: Totally enclosed, double break, silver-cadmium oxide; assembled to allow inspection and replacement without disturbing line or load wiring.

      - Control Circuits: 120-V ac; obtained from integral CPT, with primary and secondary fuses, with CPT of sufficient capacity to operate integral devices and remotely located pilot, indicating, and control devices.

        - CPT Spare Capacity: Size CPT at least one size above minimum VA requirements.

      - Compelling relays shall ensure that motor will start only at low speed.

      - Accelerating timer relays shall ensure properly timed acceleration through speeds lower than that selected.

      - Decelerating timer relays shall ensure automatically timed deceleration through each speed.

      - Melting Alloy Overload Relays:

        - Inverse-time-current characteristic.

        - Class 10 tripping characteristic.

        - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

      - Bimetallic Overload Relays:

        - Inverse-time-current characteristic.

        - Class 10 tripping characteristic.

        - Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

        - Ambient compensated.

      - Solid-State Overload Relay:

        - Switch or dial selectable for motor running overload protection. Software selectable controls are not allowed.

        - Sensors in each phase.

        - Class 10 tripping characteristic selected to protect motor against voltage and current unbalance and single phasing.

        - Class II ground-fault protection, with start and run delays to prevent nuisance trip on starting.

        - IP addressable communication module.

      - One each N.C. and N.O. reversible, isolated overload alarm contact.

      - External overload reset push button.

    - Combination Multispeed Magnetic Controller: Factory-assembled combination of reduced-voltage magnetic controller, OCPD, and disconnecting means.

      - Fusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate indicated fuses.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - Nonfusible Disconnecting Means:

        - NEMA KS 1, heavy-duty, horsepower-rated, nonfusible switch.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

        - Auxiliary Contacts: Minimum two N.O./N.C. reversible contacts, arranged to activate before switch blades open.

      - MCP Disconnecting Means:

        - Use where available fault current is 65,000 Amps symmetrical or less.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable up to 1300% of motor FLA, short-circuit trip coordinated with motor locked-rotor amperes.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

      - MCCB Disconnecting Means:

        - Use where available fault current is greater than 65,000 Amps symmetrical.

        - UL 489, UL 489, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

        - Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

        - Lockable Handle: Accepts 3/8 inch hasp padlocks and interlocks with cover in closed position.

  - VARIABLE-FREQUENCY CONTROLLERS

    - Refer to Section 26 29 23 - Variable Frequency Controllers.

  - ACCESSORIES

    - Devices shall be factory installed in controller enclosure, unless otherwise indicated.

Delete paragraphs and associated subparagraphs below if not applicable. Coordinate with Drawings.

    - Push-Buttons, Pilot Lights, and Selector Switches: NEMA ICS 2, heavy-duty, industrial oil-tight type.

      - Push Buttons: 120V, 20A, industrial grade, nylon, NEMA 13.

      - Pilot Lights: 120V LED transformer types, red “running” and green “ready”, push to test, mounted in front panel of each module.

      - Selector Switches: Rotary hand-off-auto mounted in front panel.

    - Stop and Lockout Push-Button Station: Momentary-break, push-button station with a factory-applied hasp arranged so padlock can be used to lock push button in depressed position with control circuit open.

    - Control Relays: Auxiliary and adjustable time-delay relays.

    - Elapsed Time Meters: Heavy duty with digital readout in hours.

    - Meters: Panel type, 2-1/2-inch minimum size with 90- or 120-degree scale and plus or minus two percent accuracy. Where indicated, provide selector switches with an off position.

    - Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays as required by engineering considerations: Solid-state sensing circuit with isolated output contacts for hard-wired connection. Provide adjustable undervoltage setting.

    - Breather and drain assemblies, to maintain interior pressure and release condensation in Type 4 and Type 4X enclosures installed outdoors or in unconditioned interior spaces subject to humidity and temperature swings.

    - Space heaters, with N.C. auxiliary contacts, to mitigate condensation in enclosures installed outdoors.

    - Spare control wiring terminal blocks, quantity as indicated; unwired.

Use paragraph below with three external current transformers.

    - Current-Sensing, Phase-Failure Relays: Solid-state sensing circuit with isolated output contacts for hard-wired connection; arranged to operate on phase failure, phase reversal, current unbalance of from 30 to 40 percent, or loss of supply voltage; with adjustable response delay.

  - FACTORY FINISHES

    - Finish: Manufacturer’s standard paint applied to factory-assembled and tested enclosed controllers before shipping.

- EXECUTION

  - EXAMINATION

    - Examine areas to receive enclosed controllers for compliance with working space requirements of NEC Article 110-26, installation tolerances, and other conditions affecting performance.

    - Examine enclosed controllers before installation. Reject enclosed controllers that are wet, moisture damaged, or mold damaged.

    - Proceed with installation only after unsatisfactory conditions have been corrected.

  - APPLICATIONS

    - Select features of each enclosed controller to coordinate with ratings and characteristics of supply circuit and motor; required control sequence; duty cycle of motor, drive, and load; and configuration of pilot device and control circuit affecting controller functions.

    - Select horsepower rating of controllers to suit motor controlled.

  - CONTROLLER INSTALLATION

    - For control equipment at walls, bolt units to wall or mount on lightweight structural-steel channels bolted to wall. For controllers not at walls, provide freestanding racks complying with Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

    - Install freestanding equipment on concrete bases complying with Section 03 30 00 - Cast-in-Place Concrete.

    - Enclosed Controller Fuses: Install fuses in each fusible switch. Comply with requirements in Section 26 28 13 - Fuses.

    - Floor-Mounted Controllers: Install enclosed controllers on 3-1/2 -inch nominal-thickness concrete base. Concrete shall be rated minimum 3000 psi.

      - Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch centers around the full perimeter of concrete base.

      - For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

      - Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

      - Install anchor bolts to elevations required for proper attachment to supported equipment.

    - Seismic Bracing: Comply with requirements specified in Section 26 05 48 - Seismic Controls for Electrical and Communication Work.

    - Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

    - For individual magnetic motor starters, provide an overcurrent protection and disconnect device ahead of controller. This device shall be in an enclosure with lockout means.

    - Torque all lugs per manufacturer’s written recommendations. When manufacturer’s recommendations are unavailable, use UL 486A and UL 486B for torque values.

      - Place a spot of red paint on lugs after torqueing such that paint will be visibly disturbed if lugs are disturbed.

    - Install fuses in each fusible-switch enclosed controller.

    - Install fuses in control circuits if not factory installed. Comply with requirements in Section 26 28 13 - Fuses.

    - Install heaters in thermal overload relays. Select heaters based on actual nameplate full-load amperes after motors have been installed.

    - Install, connect, and fuse thermal-protector monitoring relays furnished with motor-driven equipment.

    - Install power factor correction capacitors. Connect to the line or load side of overload relays as required by project parameters. If connected to the load side of overload relays, adjust overload heater sizes to accommodate the reduced motor full-load currents.

    - Comply with NECA 1.

  - CONTROL WIRING INSTALLATION

Delete this Article if not applicable or if remote control or indication is not required.

    - Install wiring between motor-control devices according to Section 26 05 19 - 600 Volt or Less Wire and Cable.

    - Bundle, train, and support wiring in enclosures.

    - Connect hand-off-automatic switch and other automatic-control devices where applicable.

      - Connect selector switches to bypass only manual- and automatic-control devices that have no safety functions when switch is in hand position.

      - Connect selector switches with enclosed controller circuit in both hand and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

      - Provide auxiliary switch operated by disconnect switch mechanism to remove all foreign control power when disconnect switch is open.

  - CONNECTIONS

    - Conduit installation requirements are specified in other Division 26 Electrical Sections. Drawings indicate general arrangement of raceways.

    - Ground equipment.

    - Tighten electrical connectors and terminals according to manufacturer’s published torque-tightening values. If manufacturer’s torque values are not indicated, use those specified in UL 486A and UL 486B.

      - Mark lugs after torquing with red paint such that paint will be visibly disturbed if lugs are disturbed.

  - IDENTIFICATION

    - Identify enclosed controller components and control wiring according to Section 26 05 53 - Electrical Identification.

    - Label motor controller with engraved laminated-plastic nameplate with equipment designation, power source, source location, voltage/phase, load designation, location and horsepower.

    - Provide typed label inside motor controller door identifying motor nameplate horsepower, full-load amperes, code letter, service factor and voltage/phase rating.

    - Equipment used in emergency systems shall be labeled “Suitable for use on emergency systems” per NEC 700-3.

  - FIELD QUALITY CONTROL

    - Manufacturer’s Field Service: Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including pre-testing and adjusting solid-state controllers.

    - Prepare for acceptance tests as follows:

      - Remove all blocking used for shipment.

      - Test insulation resistance for each motor controller component, connecting supply, feeder, and control circuit. Use a 500-Volt Megger for 208- and 240-Volt systems, and a 1000-Volt Megger for 480-Volt systems.

      - Test continuity of circuit and equipment ground.

      - Verify proper rating of overcurrent protective device.

      - Verify correct conductor color-coding.

      - Verify that voltages at controller locations are within plus or minus 10 percent of motor nameplate rated voltages. If outside this range for any motor, notify the Engineer before starting the motor(s).

      - With motor disconnected, energize control circuit and test for correct functioning.

        - Control switch test:

          - Inspect all contacts and shunts. Clean contacts if required.

          - Operate switch and note that all design functions are performed in proper sequence.

        - Check all auxiliary contacts for correct arrangement with coil de-energized (normally open or normally closed).

      - Check all motor for proper phase rotation.

    - Testing: Perform the following field quality-control testing:

      - Perform each electrical test and visual and mechanical inspection indicated in NETA ATS, Section 7.16.1.

      - Perform the following infrared (thermographic) scan tests and inspections and prepare reports:

        - Initial Infrared Scanning: After Substantial Completion, but not more than two weeks prior to Final Acceptance, perform an infrared scan of each multi-pole enclosed controller. Remove front panels so joints and connections are accessible to portable scanner.

        - Follow-up Infrared Scanning: The Port shall have the option of performing its own infrared scan.

      - Certify compliance with test parameters.

      - Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

    - Test Reports: Prepare a written report to record the following:

      - Test procedures used.

      - Test results that comply with requirements.

      - Test results that do not comply with requirements and corrective action taken to achieve compliance with requirements.

  - ADJUSTING

Paragraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

    - Set field-adjustable switches and circuit-breaker trip ranges.

    - Set motor circuit protectors as low as possible without causing nuisance tripping.

    - Set motor overloads per manufacturer’s tables for actual motor nameplate full-load amperes.

      - Where motor controllers with CT/Microprocessor overloads are employed, set all adjustable parameters per Engineer’s instructions.

    - Adjust overload-relay heaters or settings if power factor correction capacitors are connected to the load side of the overload relays.

    - Adjust the trip settings of MCPs and thermal-magnetic circuit breakers with adjustable instantaneous trip elements. Initially adjust to six times the motor nameplate full-load ampere ratings and attempt to start motors several times, allowing for motor cooldown between starts. If tripping occurs on motor inrush, adjust settings in increments until motors start without tripping. Do not exceed eight times the motor full-load amperes (or 11 times for NEMA Premium Efficient motors if required). Where these maximum settings do not allow starting of a motor, notify the Engineer before increasing settings. If initial setting of six times the motor nameplate FLA rating does not cause tripping, adjust settings down so that setting is as low as possible without causing nuisance tripping.

    - Set the taps on reduced-voltage autotransformer controllers as required as part of field certification.

    - Set field-adjustable switches and program microprocessors for required start and stop sequences in reduced-voltage solid-state controllers.

    - Where motor controllers with CT/Microprocessor overloads are provided, set all adjustable parameters per Engineer’s instructions.

    - Set field-adjustable circuit-breaker trip ranges as specified in Section 26 05 72 – Short Circuit, Coordination, and Arc Flash Study.

  - CLEANING

    - Clean enclosed controllers internally, on completion of installation, according to manufacturer’s written instructions. Vacuum dirt and debris; do not use compressed air to assist in cleaning.

  - STARTUP SERVICE

Delete first paragraph below if factory-authorized service representative is not required.

    - Engage a factory-authorized service representative to perform startup service.

    - Verify that enclosed controllers are installed and connected according to the Contract Documents.

    - Verify that electrical wiring installation complies with manufacturer’s submittal and installation requirements in Division 26 Electrical Sections.

    - Complete installation and startup checks according to manufacturer’s written instructions.

  - DEMONSTRATION AND TRAINING

This section may not be required for simple FVNR controllers with start-stop control.

    - Engage a factory-authorized service representative to train Port maintenance personnel to adjust, operate, and maintain enclosed controllers.

      - Train Port maintenance personnel on procedures and schedules for starting and stopping, troubleshooting, servicing, and maintaining equipment and schedules.

      - Review data in maintenance manuals. Refer to Section 01 78 23 - Operations and Maintenance Data.

      - Schedule training with the Port with at least seven days’ advance notice.

  - OPERATION AND MAINTENANCE MANUALS

    - Comply with Section 01 78 23.13 - Operations and Maintenance Data and Part 1 of this specification.

- MEASUREMENT AND PAYMENT

  - GENERAL

    - No separate measurement or payment will be made for the Work required by this section. The cost for this portion of the Work will be considered incidental to, and included in the payments made for the applicable bid items in the [Schedule of Unit Prices] [Lump Sum price bid for the Project].

End of Section

Revision History:

05/01/2014 Conversion to 2004 CSI Numbering System

10/15/2014 Added Sole Source and Salient Characteristics Note to Part 2 and revisions

01/29/2015 Changed Specification Section Number